### SECTION V.3 TECHNICAL DATA SHEETS

TABLE OF CONTENTS

SECTION V.3 TECHNICAL DATA SHEETS	2

1.	220kV Circuit Breaker	3

2.	220kV Disconnector and Earthing switch	8

3.	220kV Current Transformer	13

4.	220kV SURGE ARRESTER	16

5.	220kV Suspension and Tension Insulator	19

7.	Thermal Resistant Aluminium Alloy Conductor, Steel Reinforced (TACSR)	21

8.	Thermal Aluminium Conductor (TAL 850)	23

9.	Jessamine 1750MCM AAC All Aluminum Conductor	24

10.	HV Connector	25

- SECTION V.3 TECHNICAL DATA SHEETS

220kV Circuit Breaker

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 62271-100, IEC 62271-1 |  |
| 5 | Type | Outdoor, Single-pole operation |  |
| 6 | Insulation environment | SF6 |  |
| 7 | Rated voltage | 245 kV |  |
| 8 | Rated frequency | 50 Hz |  |
| 9 | Rated current: | 2000A |  |
| 10 | Rated short-time withstand current |  |  |
|  | Phu Lam s/s | ≥ 63kA rms |  |
|  | Hoc Mon s/s | ≥ 50kA rms |  |
| 11 | Rated peak withstand current |  |  |
|  | Phu Lam s/s | ≥ 157,5kA rms |  |
|  | Hoc Mon s/s | ≥ 125kA rms |  |
| 12 | Rated duration of short circuit | ≥ 1 s |  |
| 13 | Rated Operating Sequence | O-0.3s-CO-3min-CO |  |
| 14 | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | ≥ 1050 kV peak |  |
| 15 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | ≥ 460 kV rms. |  |
| 16 | First-pole-to-clear factor | 1,3 |  |
| 17 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 18 | Out of phase breaking current time | ≤ 0,004s |  |
| 18 | Operating mechanism | Single pole |  |
| 19 | Operating mechanism drive type | Spring |  |
| 20 | Minimum clearance between phases | ≥ 2100 mm |  |
| 21 | Minimum clearance from phase to earth | ≥ 2100 mm |  |
| 22 | Operating times: |  |  |
|  | - Opening time | < 35 ms |  |
| 24 | Rated line-charging breaking current | ≥ 125 Arms |  |
| 25 | Rated cable-charging breaking current | ≥ 250 Arms |  |
| 26 | Rated capacitive breaking current | ≥ 400 Arms |  |
| 27 | DC component of short-circuit breaking current | Stated by Bidder |  |
| 28 | Resistance of the main circuit | Stated by Bidder |  |
| 29 | Type of charging | Spring (with charging indicator, charging manually and by motor) |  |
| 30 | Maximum sound level of Circuit breaker according to IEC 62271-37-082 when operating | Stated by Bidder |  |
| 31 | On/Off indicator | Yes |  |
| 32 | TRV peak value of transient recovery voltage |  |  |
|  | Terminal fault | 364kV |  |
|  | Short-line fault | 280kV |  |
|  | Out-of-phase | 500kV |  |
| 33 | Rate of rise recovery voltage (RRRV) | To be in accordance with IEC 62271-100 and Bidder have to state general capability and full test data. |  |
| 34 | Number of tripping coil | 2 |  |
| 35 | Number of closing coil | 1 |  |
| 36 | Mechanical operation duration without maintenance | ≥ 10.000 cycles (closing-opening) |  |
| 37 | Number of Closing - Opening times at 100% rated current | ≥ 2.500 times |  |
| 38 | Times of tripping the 100% rated short-time withstand current | ≥ 10 |  |
| 39 | Times of tripping the 50% rated short-time withstand current | ≥ 30 |  |
| 40 | Support insulator |  |  |
|  | Applicable standard | IEC 62155 or equivalent |  |
|  | Materials | Porcelain, brown |  |
|  | Minimum creepage distance | 25mm/kV |  |
|  | Total creepage distance (mm) | Stated by Bidder |  |
|  | Maximum load when operating (kN) | Stated by Bidder |  |
|  | Load withstanding capability of pole, kN | Stated by Bidder |  |
| 41 | Interrupting chamber system: |  |  |
|  | There shall be devices for dehumidifier, absorbing decomposition substances. Releasing internal high pressure device may be additionally equipped. | Yes |  |
|  | Connection of support insulators; or of other parts is bolts | Yes |  |
| 42 | Tripping and arc-extinguishing compartment |  |  |
|  | Construction of Arc-extinguishing compartment | Live tank |  |
|  | Quantity of Arc-extinguishing compartment | 1 |  |
|  | First-pole-to-clear factor, pu | 1,3 |  |
|  | Terminal fault | 1,3 |  |
|  | Short-line fault | 1 |  |
|  | Out-of-phase | 2 |  |
|  | Arc-extinguishing Environment | SF6 |  |
|  | Quantity of closing coil per phase | 01 |  |
|  | Quantity of tripping coil per phase | 02 |  |
| 43 | Number of spare auxiliary contact |  |  |
|  | Normal opening contact | ≥12 |  |
|  | Normal closing contact | ≥12 |  |
| 44 | SF6 system |  |  |
|  | - Density indicator: |  |  |
|  | + Heat compensation type | Yes |  |
|  | + Quantity: 03 pieces (single-pole circuit breaker) or 01 piece (three-pole circuit breaker) | Yes |  |
|  | + Including warning circuit of SF6 at Level 1 and Level 2. | Yes |  |
|  | - One-way valve for filling and releasing SF6 | Yes |  |
|  | - Loss-rate per year | ≤ 0,5% |  |
|  | - Purity | ≥ 98,5% |  |
|  | - Dew point | Comply with IEC 60376 |  |
|  | - Total mass of SF6 for Circuit breaker | Stated by Bidder |  |
|  | - Rated density of SF6 | Stated by Bidder |  |
|  | - Level 1 density | Stated by Bidder |  |
|  | - Level 2 density | Stated by Bidder |  |
| 45 | Local control cubicle: |  |  |
|  | - Material of enclosure | Aluminum alloy or stainless steel |  |
|  | - Minimum protection class | IP55 |  |
|  | - Minimum thickness of enclosure | ≥ 2mm |  |
|  | - Local/remote switch | Yes |  |
|  | - Mechanism for opening/closing Circuit breaker | Yes |  |
|  | - Counter | Yes |  |
|  | - Functional circuits (such as monitoring tripping coil circuit, power supply status, spring charging…) | Yes |  |
|  | - Anti-pumping circuit | Yes |  |
|  | - Out-of-phase protection circuit | Yes |  |
|  | - Over-voltage and Overload protection circuit for motor | Yes |  |
|  | - Spring charge indicator | Yes |  |
|  | - Heat system, Led light system, Miniature circuit breaker | Yes |  |
|  | - Charging spring | Manually and motor |  |
|  | - Maximum time for charging | 15s |  |
| 46 | Auxiliary power supply |  |  |
|  | - Heating and lighting system | 220VAC (+10%; -15%) |  |
|  | - Tripping voltage | 220VDC (+10%; -30%) |  |
|  | - Closing circuit | 220VDC (+10%; -25%) |  |
|  | - Motor for charging spring | 220VDC (+10%; -15%) (it is recommended to equipped additionally the 220VAC (+10%;-15%)) |  |
|  | - Total burden of tripping coils or that of closing coils of three phases | < 1200VA |  |
| 47 | Materials of steel structure (if any) | Galvanized steel |  |
| 48 | Terminal connector |  |  |
|  | Materials | Aluminum alloy |  |
|  | Dimension | Suitable for conductor |  |
|  | Bolts for terminal connector | Stainless steel or other suitable materials |  |
| 49 | Technical documents | English/Vietnamese |  |
| 50 | Requirements for testing (according to Technical Specification) | Comply |  |
| 51 | The other specification shall comply with stipulation in Letter No. 1677/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT | Yes |  |

220kV Disconnector and Earthing switch

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number: |  |  |
| 2.1 | Three-pole Dis-connector with two ES | Stated by Bidder |  |
| 2.2 | Three-pole Dis-connector with one ES | Stated by Bidder |  |
| 2.3 | Three-pole Dis-connector no ES | Stated by Bidder |  |
| 2.4 | One-pole Dis-connector | Stated by Bidder |  |
| 3 | Applicable standard | IEC 62271-102 |  |
| 4 | Rated frequency | 50 Hz |  |
| 5 | Neutral system | Directly earthed |  |
| 6 | Type | Outdoor, center-break, three-poles/one-pole, horizontal rotary type |  |
| 7 | Voltage specification of DS: |  |  |
| 7.1 | Nominal voltage of system | 220kV |  |
| 7.2 | Maximum operating voltage of system | 242kV |  |
| 7.3 | Rated voltage | 245kV |  |
| 7.4 | Rated short-duration power-frequency withstand voltage of DS: + Phase-to-Earth + Between phases | ≥ 460 kV |  |
|  | Across the isolating distance | ≥ 530 kV |  |
| 7.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Between phases | ≥ 1050 kV (p) |  |
|  | Across the isolating distance | ≥ 1200 kV (p) |  |
| 8 | Current specification of DS: |  |  |
| 8.1 | Rated normal current (Ir) | ≥ 2000 A |  |
| 8.2 | Rated short-time withstand current |  |  |
|  | Phu Lam s/s | ≥ 63 kA rms |  |
|  | Hoc Mon s/s | ≥ 50 kA rms |  |
| 8.3 | Rated duration of short-circuit | ≥ 1s |  |
| 8.4 | Rated peak withstand current |  |  |
|  | Phu Lam s/s | ≥ 157,5kA (p) |  |
|  | Hoc Mon s/s | ≥ 125kA (p) |  |
| 8.5 | Resistance of the main circuit | Stated by Bidder |  |
| 9 | Specification of ES: |  |  |
| 9.1 | Rated short-circuit making current |  |  |
|  | Phu Lam s/s | ≥ 63 kA rms |  |
|  | Hoc Mon s/s | ≥ 50 kA rms |  |
| 9.2 | Rated induced current of electrostatic coupling of ES on the line side | 3A rms |  |
| 9.3 | Rated induced current of electromagnetic coupling of ES on the line side | 80A rms |  |
| 9.4 | Rated withstand voltage between insulated terminals and bases earthed | ≥ 283kV |  |
| 10 | Operation ability of DS, ES: |  |  |
| 10.1 | Mechanical structure | Single pole/3 poles |  |
| 10.2 | Mechanical endurance: |  |  |
| 10.2.1 | DS | M1 class |  |
| 10.2.2 | ES | M0 class |  |
| 10.3 | Quantity of closing/opening times without maintenance: |  |  |
| 10.3.1 | DS | ≥ 2000 |  |
| 10.3.2 | ES | ≥ 1000 |  |
| 10.4 | Crank for manual opening/closing DS and ES | Yes |  |
| 10.5 | Mechanical interlocking structure between DS and ES | Yes |  |
| 11 | Total weight | Stated by Bidder |  |
| 12 | Safety clearance: |  |  |
| 12.1 | Between phases | ≥ 2100 mm |  |
| 12.2 | Between phase and earth | ≥ 2100 mm |  |
| 13 | Support insulator: |  |  |
| 13.1 | Applicable standard | IEC 60273 or equivalent |  |
| 13.2 | Material | Brown porcelain |  |
| 13.3 | Creepage distance | ≥ 25mm/kV |  |
| 13.4 | Total creepage distance | Stated by Bidder |  |
| 13.5 | Load bearing capability at pole of DS: | Stated by Bidder |  |
| 13.5.1 | For three-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 0,8 (for rated current ≤ 2500A) 1 (for rated current > 2500A) |  |
|  | Cross load (kN) | 0,27 (for rated current ≤ 2500A) 0,33 (for rated current > 2500A) |  |
| 13.5.2 | For one-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 1,25 (for rated current ≤ 2500A) 1,6 (for rated current > 2500A) |  |
|  | Cross load (kN) | 0,4 (for rated current ≤ 2500A) 0,5 (for rated current > 2500A) |  |
| 13.5.3 | Vertical force | 1,25kN |  |
| 13.6 | Maximum load when operating | Stated by Bidder |  |
| 13.7 | Minimum clearance at static state: |  |  |
| 13.7.1 | Between phase and earth | 2100mm |  |
| 13.7.2 | Between 02 poles of 01 phase | 2100mm |  |
| 14 | Materials of main contact | Copper, copper alloy or silver/nickel plated aluminum alloy |  |
| 15 | Mechanical structure: |  |  |
| 15.1 | DS | Motor driver and Manual |  |
| 15.2 | ES | Manual and Motor driver |  |
| 16 | Local control cubicle of DS and ES: |  |  |
| 16.1 | Enclosure | Aluminum alloy or stainless steel (Inox 304) or galvanized steel with suitable paint |  |
| 16.2 | Minimum protection class | IP55 |  |
| 16.3 | Minimum thickness of enclosure | ≥ 2mm |  |
| 16.4 | Normal opening auxiliary contacts of DS | ≥ 12 |  |
| 16.5 | Normal closing auxiliary contacts of DS | ≥ 12 |  |
| 16.6 | Normal opening limit switch contacts of DS | ≥ 2 |  |
| 16.7 | Normal closing limit switch contacts of DS | ≥ 2 |  |
| 16.8 | Normal opening contact of ES | ≥ 8 |  |
| 16.9 | Normal closing contact of ES | ≥ 8 |  |
| 16.10 | Permissible long-term DC current of auxiliary contacts | 10A |  |
| 16.11 | Capability of withstanding the short-term DC current of auxiliary contacts | 100A/30ms |  |
| 16.12 | Remote/Local key switch | Yes |  |
| 16.13 | Opening/closing DS and ES switch | Yes |  |
| 16.14 | Individual auxiliary contacts for power supply of motor and MCBs | Yes |  |
| 16.15 | Over-load and over-current protection for motor | Yes |  |
| 16.16 | Heating system with sensor, led light, MCBs with individual auxiliary contacts for power supply of heating circuit and lighting circuit | Yes |  |
| 16.17 | Electrical interlocking between DS and ES | Yes |  |
| 17 | Operating voltage |  |  |
| 17.1 | Motor driver voltage | 220VDC (+10%; -15%) |  |
| 17.2 | Heating and lighting voltage | 220VAC (+10%; -15%) |  |
| 17.3 | Control of opening/closing DS, ES | 220VDC (+10%; -15%) |  |
| 18 | Steel supporting structure (if any) |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
| 19 | Terminals connector |  |  |
| 19.1 | Materials | Aluminum/copper alloy |  |
| 19.2 | Dimensions | Fit with conductor/bus-bar |  |
| 19.3 | Bolts for terminal connector | Stainless steel or other suitable materials |  |
| 20 | Technical documents | English/Vietnamese |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Letter No. 1676/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT | Yes |  |

220kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | 60044-1 (2003-02); IEC 60815 (2008-10); IEC 60071-1 (2011-03); IEC 60137 (2008-07); IEC 61869-1 (2007-10); IEC 61869 -2 (2012-09); IEC 60060 (2010- 11); IEC 60529 (2001-02); IEC 60296 (2012-02); IEC 60422 (2013-01); IEC 60028 (1925) |  |
| 4 | Type | Outdoor, single phase, oil-immersed, Top core, directly earthed |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7 | Impulse Voltage (1.2/50s) withstand | ≥ 1050 kVpeak |  |
| 8 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | ≥ 460 kVrms |  |
|  | - Secondary windings | ≥ 3 kVrms |  |
| 9 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 10 | Rated Transformation Ratios: |  |  |
|  | Phu Lam substation | 800-1200-1600-2000/1A |  |
|  | Hoc Mon substation | 800-1200-2000/5A |  |
| 11 | Rated Thermal withstand Current |  |  |
|  | Phu Lam s/s | ≥ 63 kA rms |  |
|  | Hoc Mon s/s | ≥ 50 kA rms |  |
| 12 | Rated duration of short-circuits | ≥ 1s |  |
| 13 | Rated Dynamic Withstand Current |  |  |
|  | Phu Lam s/s | ≥ 157,5kA (p) |  |
|  | Hoc Mon s/s | ≥ 125kA (p) |  |
| 14 | Maximum Partial Discharge Level | Comply with IEC 61869-1 |  |
| 15 | Dielectric dissipation factor (tanδ) |  |  |
|  | - Un /3 | Comply with IEC 61869-2 |  |
| 16 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
| 16.1 | Phu Lam substation (Type 1) |  |  |
|  | -Core No. 1 | 800-1200-1600-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 800-1200-1600-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
|  | -Core No. 4 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
| 16.2 | Phu Lam substation (Type 2) |  |  |
|  | -Core No. 1 | 800-1200-1600-2000/1A 10VA - Cl 0.2 |  |
|  | -Core No. 2 | 800-1200-1600-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
|  | -Core No. 4 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-1600-2000/1A 30VA - 5P20 |  |
| 16.3 | Hoc Mon substation |  |  |
|  | -Core No. 1 | 800-1200-2000/5A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 800-1200-2000/5A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-2000/5A 30VA - 5P20 |  |
|  | -Core No. 4 | 800-1200-2000/5A 30VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-2000/5A 30VA - 5P20 |  |
| 17 | Temperature rise limit of windings | 650C |  |
| 18 | Minimum creepage distance | ≥25 mm/kV |  |
| 19 | Transforming current performed at Secondary winding | Yes |  |
| 20 | Static load-bearing capacity | Comply with IEC 60044-1 and IEC 61869-1 |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Letter No. 1819/QĐ-EVNNPT dated 16/09/2025 issued by EVNNPT | Yes |  |

220kV SURGE ARRESTER

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacture/Country of Origin | Stated by Bidder |  |
|  | Ordering number | Stated by Bidder |  |
|  | Applicable standard | IEC 60099-4; IEC 60071-1:2019; IEC 60137: 2017; IEC 62039; IEC/TS 60815-3 (2008-10); IEC/TS 60815-3 (2008-10) |  |
|  | Nominal voltage, kV | 220 |  |
|  | Maximum operating voltage of SA, kV | 245 |  |
|  | Method of neutral grounding | Directly earthed |  |
|  | Type of SA | Outdoor installation |  |
|  | Permissible overvoltage factor for single-phase grounding | 1,4 |  |
|  | Surge arrester connection mode | Phase- earth |  |
|  | Technical specifications of surge arresters |  |  |
|  | Category | Outdoor, ZnO, gapless |  |
|  | Rated voltage (Ur) | 192 kV |  |
|  | Minimum continuous operating voltage (Uc) | 152 kV |  |
|  | Temporary overvoltage with TOV characteristic curve, kVrms | Stated by Bidder |  |
|  | Nominal discharge current (In) | ≥ 10 kA |  |
|  | Peak discharge current, kApeak | ≤ 100 |  |
|  | Minimum energy absorption capability (Wth) at rated voltage | ≥ 7kJ/kV |  |
|  | Repeated discharge capability - Qrs, C | ≥ 1,6 |  |
|  | Equipotential ring | Stated by bidder |  |
|  | Technical specifications of the surge arrester housing |  |  |
|  | Housing materials | Porcelain or polymer |  |
|  | Rated short-duration power-frequency withstand voltage | ≥ 460 kV |  |
|  | Rated lightning impulse withstand voltage (1,2/50 µs-BIL), kV peak | ≥ 1050 kV peak |  |
|  | - Minimum creepage distance | > 25 mm/kV |  |
|  | Rated short-circuit withstand current, kA | ≥ 63kA |  |
|  | Specified long term load, kN | ≥ 400 |  |
|  | Specified short term load, kN | ≥ 1000 |  |
|  | Mean breaking load, kN | ≥ 1200 |  |
|  | Accessories of surge arresters |  |  |
|  | Lightning counter with leakage current display | Yes |  |
|  | Number of digits of the lightning counter | ≥ 5 |  |
|  | Leakage current measurement range, mA | Stated by Bidder |  |
|  | Sensitivity to lightning surge, A | ≤ 200 |  |
|  | Surge current withstand capability (4/10 μs), kA | ≥ 100 |  |
|  | Minimum protection rating of the lightning counter enclosure | IP54 |  |
|  | Steel supporting structure | Galvanized steel with a minimum coating thickness of 80μm |  |
|  | HV terminal: | 01 terminal/ 01 SA |  |
|  | Materials | Compatible with the designed conductors |  |
|  | Dimensions | Compatible with the designed conductors |  |
|  | Bolts of HV terminal | Stainless steel or hot-dip galvanized steel |  |
|  | Accompanying technical documentation clearly showing bid specifications, dimensional drawings, installation instructions, operation guidelines, and maintenance procedures | Yes |  |
|  | Steel supporting structure |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
|  | Leakage current meter shall be capable of communicating with computer control system in control room of substation for online monitoring leakage current. The Bidder shall supply all accessories for connecting and transmitting signals from Leakage current meter to computer control system in control room of substation, such as optical cable, ODF box, optical converter, switching power supply adapter (if any),... | yes |  |
|  | The other specification shall comply with specification in Decision No. 1158/QĐ-EVNNPT dated 27/06/2025 of EVNNPT | yes |  |

220kV Suspension and Tension Insulator SET:

- 5.1 INSULATOR:

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacture/Country of Origin | To be specified |  |
|  | Ordering number | To be specified |  |
|  | Applicable standard | IEC 60305 |  |
|  | Type of insulator | Outdoor, Toughened glass/porcelain insulator with ball and socket coupling |  |
|  | + Type 1 (Tension insulator set) | U120BP |  |
|  | + Type 2 (Suspension insulator set) | U70BLP |  |
|  | Type of coupling | Ball and socket |  |
|  | Size of coupling | 16 mm |  |
|  | Minimum breaking strength | Type 1: ≥ 120 kN |  |
|  |  | Type 2: ≥ 70 kN |  |
|  | Max nominal diameter of insulating part | 280 mm |  |
|  | Nominal Spacing | 146 mm |  |
|  | Min Power Frequency Withstand Voltage |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | Type 1: 85 kV Type 2: 80 kV |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | Type 1: 50 kV Type 2: 50 kV |  |
|  | Dry lightning Impulse Withstand Voltage | ≥ 125 kV |  |
|  | Minimum puncture voltage | 130kV |  |
|  | Minimum nominal creepage distance | 440mm |  |
|  | Zinc sleeve on pin | Yes |  |
|  | Weight | Stated by Bidder |  |
|  | Number of insulator per insulator set | 16 |  |
|  | Fixing type to Gantry beam | Shackle (socket) coupling (01 point, 22) |  |
|  | Minimum Failing Load-bending (Electromechanical failing load) | Type 1: ≥ 120 kN Type 2: ≥ 70 kN |  |
|  | Requirements for testing (according to Technical Specification) | Comply |  |
|  | The other specification shall comply with stipulation in Letter No. 1769/QĐ-EVNNPT dated 09/09/2025 issued by EVNNPT | Comply |  |

- Fittings for insulator set:

| No. | Description | Required | Offered and Guaranteed |
| --- | --- | --- | --- |
| - I | - Fittings for Insulator Sets |  |  |
| 1 | Manufacturer/ code | To be specified |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Safety factor | 2,5 |  |
| 5 | All steel fittings are galvanized | Yes |  |
|  | Mass of galvanized layer: | To be Comply with BS 279 |  |
|  | - Fittings, g/sq.m | 610 |  |
|  | - Bolts, nuts and washers, g/sq.m | 305 |  |
| 6 | Material to be used for: |  |  |
|  | - Hinge | Hot-dip galvanized steel |  |
|  | - Ball eyes | Hot-dip galvanized steel |  |
|  | - Ball sockets/socket clevis | Hot-dip galvanized steel |  |
|  | - U-bolts | Hot-dip galvanized steel |  |
|  | - Adjustable extension links | Hot-dip galvanized steel |  |
|  | - Extension links | Hot-dip galvanized steel |  |
|  | - Yoke | Hot-dip galvanized steel |  |
|  | - Bolts and nuts, washer | Stainless steel |  |
|  | - Split pins | Stainless steel |  |
| 7 | Specified mechanical load of fittings, kN | Fit with corresponding insulation set specified in the Bidding documents |  |
| 8 | Information engraved on spacer: Name or logo of the manufacturer + code | Yes |  |
| 9 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| - II | - Arcing horn - Corona ring |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Material to be used for arcing horn | Hot-dip galvanized steel |  |
| 4 | Type of insulation set of conductors: |  |  |
|  | - Tower side | Arcing horn/ Corona ring |  |
|  | - Conductor side | Corona ring |  |
| 5 | Drawings with dimension, installation manual | Yes |  |
| III | Tension clamp |  |  |
| 1 | Manufacturer/ code | - |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Type | Tension set, compressed type with terminal jumper fixed by bolts, used for conductor |  |
| 5 | Compressed shape | Hexagon |  |
| 6 | The offered Tension clamp shall fit with the following conductors: |  |  |
|  | + TACSR 410 | Yes |  |
| 7 | Specified mechanical load of Tension clamp after compressed | ###### ≥ 90% Min. Specified mechanical load of corresponding conductor |  |
| 8 | Resistance of Tension clamp after compressed | ≤ 1,2 times of resistance of conductor with corresponding length |  |
| 9 | Information engraved on Tension clamp: name or logo of the manufacturer + code + conductor type + compressing code + position and direction of compressing | Yes |  |
| 10 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| IV | Suspension clamp |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Type | Suspension clamp type bolts, clamping part shall be fixed by 2 bolts (U shape). Body and clamping part shall be made from aluminum, aluminum alloy or soft steel that is high load-bearing and conductive, corresponding to conductor; or made by hot-dip galvanized load-bearing steel (for TK 70); be capable of resisting deforming and loose status. Surface of suspension clamp shall be so designed to ensure high exposure and conductive |  |
| 5 | The offered Suspension clamp shall fit with the following conductors: |  |  |
|  | + TACSR 410 | Yes |  |
| 6 | Information engraved on Suspension clamp: name or logo of the manufacturer + code + conductor type | Yes |  |
| 7 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| V | Spacer |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standard | IEC 61854 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | The offered Spacer damper/ Jumper spacer shall fit with the following conductors: |  |  |
|  | + TACSR 410 | Yes |  |
| 4 | Mass of Spacer damper and Jumper spacer | ###### Stated by Bidder |  |
| 5 | Body and clamping part of Spacer damper shall be made from aluminum or aluminum alloy | Yes |  |
| 6 | Bolts, nuts and washers shall be stainless | Yes |  |
| 7 | Information engraved on vibration damper: name or logo of the manufacturer + code + clamping dimension + conductor tye | Yes |  |
| 8 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |

THERMAL RESISTANT ALUMINIUM ALLOY CONDUCTOR, STEEL REINFORCED (TACSR)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | IEC 61089 |  |
|  | Type 1 |  | TACSR-810 |  |
|  | Type 2 |  | TACSR-410 |  |
|  | Nominal cross section area: |  |  |  |
|  | Type 1 | mm2 | 814.3 |  |
|  | Type 2 | mm2 | 413.5 |  |
|  | Stranded number and diameter of strands |  | To be specified |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Type 1 |  | To be specified |  |
|  | Type 2 |  | To be specified |  |
|  | Minimum strength load |  | To be specified |  |
|  | Type 1 | kN | ≥180.9 |  |
|  | Type 2 | kN | ≥136.1 |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor |  |  |  |
|  | Type 1 | kg/km | 2700 |  |
|  | Type 2 | kg/km | 1673 |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C |  |  |  |
|  | Type 1 | A | 2007 |  |
|  | Type 2 | A | 1324 |  |
|  | Overall diameter of stranded conductor |  |  |  |
|  | Type 1 | mm | To be specified |  |
|  | Type 2 | mm | To be specified |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | To be specified |  |
|  | Type 2 | daN/mm2 | To be specified |  |
|  | DC resistance at 200C |  |  |  |
|  | Type 1 | Ω/km | ≤ 0,0363 |  |
|  | Type 2 | Ω/km | ≤ 0,0714 |  |

THERMAL ALUMINIUM CONDUCTOR (TAL 850)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | IEC 61089 |  |
|  | Type |  | TAL-850 |  |
|  | Nominal cross section area: | mm2 | 845.1 |  |
|  | Stranded number and diameter of strands | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Minimum strength load | kN | ≥120.9 |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor | kg/km | 2334 |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C | A | 2073 |  |
|  | Overall diameter of stranded conductor | mm | To be specified |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | DC resistance at 200C | Ω/km | ≤ 0,0342 |  |

Jessamine 1750MCM AAC All Aluminum Conductor

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | ASTM B230, IEC 61089 |  |
|  | Type |  | Jessamine 1750MCM |  |
|  | Nominal cross section area: | MCM | 1750 |  |
|  | Stranded number and diameter of strands | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Minimum strength load | kN | To be specified |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor | kg/km | To be specified |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C | A | 1408 |  |
|  | Overall diameter of stranded conductor | mm | To be specified |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | DC resistance at 200C | Ω/km | 0.00988 |  |

HV Connector

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Ordering number |  | To be specified |  |
|  | Applicable standard |  | IEC 694, NEMA CC1 or equivalent |  |
|  | Type |  | Aluminium alloy |  |
|  | Slip strength of bolted connnector |  | To be specified |  |
|  | Bolt and screw of connector |  | Galvanized steel |  |
|  | Short-time withstand current |  |  |  |
|  | + Phu Lam s/s | kA/1s | 63 |  |
|  | + Hoc Mon s/s | kA/1s | 50 |  |
|  | Number holes |  | comply |  |
|  | Tightening force for bolt |  |  |  |
|  | - M10 bolt |  | To be specified |  |
|  | - M12 bolt |  | To be specified |  |
|  | - M14 bolt |  | To be specified |  |
|  | - M16 bolt |  | To be specified |  |
|  | Contact grease: |  | Yes |  |
|  | - Manufacturer/Country of Origin |  | To be specified |  |
|  | - Quantity |  | Conformity with connector |  |
|  | Requirements for testing (according to item 4.11) |  | Yes |  |
|  | Catalogue |  | Yes |  |