TABLE OF CONTENTS

SECTION V.2 TECHNICAL SPECIFICATIONS	2

- SECTION V.2 TECHNICAL SPECIFICATIONS

# OVERVIEW OF THE PROJECT AND THE THIS PACKAGE

## PROJECT NAME:

500kV Quynh Luu substation and Connection.

## OBJECTIVES OF THE PROJECT:

The construction of 500kV Quynh Luu substation and Connection is built to:

- Meeting the electricity supply demand for urban areas, industrial zones of Quynh Luu province and loads in the region.

- Strengthening the interconnection of the regional power system, improving safety, reliability, and stability in the operation of both the regional and national power systems.

- Reducing power losses on the transmission grid, increasing the efficiency of electricity production and business of EVN and EVNNPT.

## CONTENTS AND SCALE OF CONSTRUCTION INVESTMENT:

The project of 500kV Quynh Luu substation is planned to be built with the following scale:

### Substation part

- Voltage range: 500kV, 220kV, 35kV.

- Capacity 500 kV: 1,800 MVA: installation 01 MBA AT1 500kV-900MVA and installation 02 MBA AT2&AT3 500kV-450MVA.

- 500kV side: Equipment installation shall follow a 3/2 busbar scheme with five modules; during this phase, four line bays and three transformer bays will be installed.

- 220kV side: total 21 bays and Bus section, this stage installs 09 bays.

- Side 35kV:

- 35kV side: take from the triangle coil of the transformer 500/220/35kV-450MVA to power the 35/0.4kV-560kVA auxiliary transformer.

- Backup auxiliary power is taken from the local grid (branching off from the existing 35kV line) to supply the second auxiliary transformer 35/0.4kV-560kVA.

## LOCATION OF THE PROJECT:

- The location of 500kV Quynh Luu substation and the connection line planned to be built are selected at the Quynh Tam commune, Nghe An province.

## PROJECT MANAGEMENT:

- Investor:

- National Power Transmission Corporation (EVNNPT).

- The Northern Power Projects Management Board (NPMB) directly manages the project on behalf of EVNNPT.

- Design Consultancy Contractor:

- Power Engineering Consulting Joint Stock Company 1 (EVNPECC1).

## SCOPE

This part of the Specification describes the technical requirements for the following equipment relating to the design, manufacturer testing, delivery, testing and commissioning for all the principal equipment and systems that make up the substation works contract.

Circuit Breaker

Disconnector

Current Transformer

Voltage Capacitor Transformer

TRV Capacitor

Surge Arrester

Post insulator

Neutral grouding reactor

Neutral resistor connected neutral reactors

Insulator

Fittings

Conductors

Lightning wires

Tubes

Terminal clamp and accessories

## STANDARDS

The equipment specified in this Specification shall conform to the latest edition of the appropriate International Electro-technical Commission (IEC) Standards, Vietnam standard and/or recognized international standards.

# Switchyard equipment for substation

## 500kV, 220kV Circuit breaker

### General

Comply with the Technical standards of 500kV outdoor circuit breakers in, Decision No. 1677/QĐ-EVNNPT date 24/08/2025, of the National Power Transmission Corporation promulgating regulations on basic technical characteristics of 500kV, 220kV, 110kV circuit breakers on the transmission grid.

Comply with the Technical standards of 220kV outdoor circuit breakers in National Electricity of Vietnam issued together with the Decision No. 1677/QĐ-EVNNPT date 24/08/2025, of the National Power Transmission Corporation promulgating regulations on basic technical characteristics of 500kV, 220kV, 110kV circuit breakers on the transmission grid and Decision No. 2416/QĐ-EVNNPT date 09/12/2025 of the National Power Transmission Corporation promulgating regulations Regarding the adjustment and amendment of the basic technical specifications for 220 kV circuit breakers and the installation of 500 kV and 220 kV surge arresters in the transmission network.

### Definition of power transmission grid circuit breaker:

- Circuit breakers on the power transmission grid are devices capable of switching high-voltage circuits in the normal operation mode and in the abnormal or breakdown operation mode of the power grid with the rated voltage level of the equipment. The circuit breaker must meet the durability for climatic and environmental conditions in Vietnam: tropicalized, suitable for installation and operating environment conditions.

- The basic standards for applying the design, manufacture and testing of circuit breakers in the power transmission grid are IEC 62271-100 and IEC 62271-1. For bypass circuit breakers for vertical compensating capacitors, the additional standard IEC 62271-109 applies. For circuit breakers for resistance additional standards IEC 62271-110.

### General requirements on standards and environment:

- The circuit breaker on the power transmission grid which is manufactured and installed must meet Vietnamese regulations and standards, electrical standards, IEC/IEEE standards and be able to work stably in working conditions, including climate and natural environment of Vietnam.

- Environment conditions:

- Altitude above sea level	: <1000 m

- Climatic condition	: Tropical

- Maximum air temperature: 45°C

- Minimum air temperature	: 0°C

- Average air temperature	: 25°C

- Maximum humidity	: 100%

- Average humidity	: 85%

- Creepage distance:

500 kV circuit breakers (31 mm/kV)

220 kV circuit breakers (25 mm/kV)

- Seismic factor 	: 0.15g

- Depending on the natural conditions of the installation location of the equipment, as defined in QCVN 02:2009/BXD , the above values of environmental conditions may change to suit the actual requirements to be applied.

- Requirements of the electrical system installing the circuit breaker

| Item | 500 kV system | 220 kV system |
| --- | --- | --- |
| Normal Voltage | 500 kV | 220 kV |
| Rated Frequency | 50 Hz | 50 Hz |
| Max operating voltage | 550 kV | 242 kV |
| Min operating voltage | 450 kV | 198 kV |
| Connection diagram | 3-phase 3-wire | 3-phase 3-wire |
| Neutral grounding mode | Direct | Direct |
| Ground fault factor of transmission grid | ≤1,4 | ≤1,4 |

### Requirements for quality certificates:

- The manufacturer must have a certificate of the quality management system (ISO 9001 or equivalent, still valid) applied to the production of the Circuit breaker. The manufacturer must have a factory testing laboratory with certified testing equipment.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, trade and technical labels, etc.

### Requirement component parts of for circuit breaker

### Circuit breaker:

- The circuit breaker is designed and manufactured in accordance with IEC 62271-100 standard so that it can be installed outdoors in the operating conditions of Vietnam's power transmission system. The circuit breakers in the power transmission grid are usually applied single-phase type, each phase has a operation mechanism. In addition to IEC 62271-100 standard, circuit breakers must meet IEC 62271-1, IEC 62271-101, IEC 60060 standards and must meet requirements for insulation strength, temperature rise during long-term operation. For circuit breakers for resistance additional standards IEC 62271-110.

- Circuit breakers are designed and manufactured to ensure safe operation under normal as well as fault conditions, to withstand atmospheric overvoltages, overvoltage phenomenon occurs when switching operation or tripping fault circuit. The technical requirements for circuit breaker voltage shall be specified in Datasheet.

- Depending on the installation location and working requirements of the breaker. The circuit breaker shall meet the requirements for long-term working current, breaking current under different operating conditions and short-circuit breaking current specified in the datasheet without exceeding the limits for allowable working temperature is specified in IEC 62271-100.

- Operating duty cycle of  circuit breakers is: O - 0.3sec - CO - 3 min. - CO with the opening/closing time specified in detail in datasheet and close or open time for three pole discrepancy is less than or equal to 4 milliseconds.

- Circuit breakers shall be properly designed and constructed so that easily inspected and quickly replaced if it has any defective/damaged of contact chambers or other components. The components parts of circuit breakers after assembly do not form holes for birds to nest that can cause of problems.

- At the 500 kV voltage level, in special cases and depending on the installation location, the circuit breaker may need to be equipped with pre-insertion resistors and parallel-connected grading capacitors in the interrupting chamber to limit the rate of rise of the recovery voltage (RRRV). The minimum number of capacitors connected in parallel per phase shall be two (02) to ensure safe and reliable operation of the circuit breaker.

- Grading Capacitor: Depending on the calculation and technological solutions of the circuit breaker manufacturer, the grading capacitor may or may not be equipped. However, the circuit breaker must meet the required TRV and RRRV values specified below for the project and other requirements stipulated in IEC 62271-100.

### Interrupting chamber

- Except for the case of series capacitor circuit breakers, 500 kV circuit breakers usually apply the number of arc chambers from 2 chambers or more depending on the working requirements of 500 kV circuit breakers. Circuit breakers with voltage level of 220 kV or less have usualy only one of arc extinguishing chamber. Circuit breakers with isolated and arc extinguish by sulphur hexafluoride (SF6) gas insulated. The arc-extinguishing chamber must meet the requirements of SF6 gas system tightness with gas leakage ≤ 0.5%/year of the entire gas volume.

- SF6 gas or insulating and arc-extinguishing materials shall meet the detailed requirements in IEC 60376 standard. All materials used in the construction of SF6 circuit breaker shall be suitable for the working conditions in the atmosphere of SF6 gas and the decomposition products of SF6. The circuit breaker shall be able to withstand the maximum pressure during operation without gas leakage or deformation damage.

- The gas system of the interrupting chamber must have a gas pressure meter with temperature compensation function, and a monitoring device to detect SF6 gas leakage at two levels: Alarm warning mode for SF6 gas density threshold at level 1, alarm warning and lock control for SF6 gas density threshold at level 2 (lockout). The mass and density of SF 6 gas , the warning levels of level 1 and level 2 mentioned above must be clearly stated on the circuit breaker nameplate.

- Each phase of the circuit breaker is equipped with one-way valve, which is convenient for filling and discharging SF6 gas.

- The contacts of circuit breaker are made of a non-abrasive material, resistant to compression contact, resistant to the high temperatures generated by arcing in the interrupting chamber and ensuring long-term operation throughout the life of the circuit breaker.

- The operating mechanism is made of non-corrosive, high-strength metal materials without rust. The operating mechanism must be equipped with an anti-skid lock which operates the mechanism. Have a closed structure so insects do not get in. The main drive rod in the CB pole is made of insulating material, has high mechanical strength, moisture resistance, resistance to SF6 gas and SF6 decomposition products.

### Insulation and poles post of circuit breaker

- Pole post and supporting porcelain post of circuit breaker must be made of non-assembled cylindrical porcelain, canopy circle, brown color according to IEC 62155 or equivalent. Porcelain must have thermal, mechanical and electrical durability, operate in accordance with the environmental conditions and technical characteristics listed in datasheet.

- In the compartments of the pole column, there must be equipped dehumidifying apparatus, decomposition product filter of SF6 gas and pressure release device to ensure the interrupting chamber does not explode when the pressure increases suddenly. Connection between poles or other parts by bolts.

- Insulation and poles post of circuit breaker are manufactured to ensure that the distances from live parts to earth and between live parts comply with the requirements detailed in datasheet.

### Requirements for control cubicle, Operating mechanism cabinet

- Operating mechanism cabinet

- Each circuit breaker shall be equipped local control cabinet with operating mechanism, control switches and corresponding relays, switches, terminal clamp for control cables, Counter of the number of closing-opening operations of the circuit breaker, LED lighting,  heating reactors with thermal relays and other ancillary equipment.

- The secondary terminal clamps must be extended at locations with multiple connections to prevent connecting multiple conductors in the same location. The number of terminal clamps  for spare at least 20% of the connected terminal. Terminal for closing circuit or tripping circuit not located close to AC or DC power terminal.

- Operating mechanism cabinet of the circuit breaker is equipped with the following parts:

+ Switch selection of LOCAL/REMOTE position (or can be installed in the control cabinet according to the manufacturer's technology).

+ Switch selection of ON/OFF position in local (or can be installed in the control cabinet according to the manufacturer's technology).

+ Counter of the number of closing - opening operations of the circuit breaker.

+ Auxiliary contact system and limit switch to control the spring motor and alarm signal the status of spring storage.

+ There is a spring charge status indicator: in the form of symbols/or letters to identify spring status of the circuit breaker is charged and not charged.

+ The indicator of the open /close status of the circuit breaker.

+ The number of auxiliary contacts in each phase of the circuit breaker must comply with the requirements in datasheet.

- The Operating mechanism shall be capable of locking at the closed or open position of the circuit breaker and shall be capable of opening or closing after recloser period.

- The Operating mechanism and associated equipment must be able to withstand the operating forces of the circuit breaker in accordance with IEC 62271-100 and have a safe mechanical operation duration of at least 10000 times.

- Having open-close status and spring charge status indicator of circuit breaker for easy identification without opening the door of the cabinet.

- The capacity of closing coil and tripping coils must not exceed 1200VA for all 3 phases. The required capacity may be greater in case of close/open time is faster than the value specified in data sheet.

- The Operating mechanism cabinet can be made of aluminum alloy or stainless steel (Inox 304) and can be painted on the surface of the cabinet in accordance with the general specifications. The Operating mechanism cabinet has a minimum thickness of 2 mm. The control cabinet must withstand extreme weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets.

- Common control cubicle

- For voltage level from 220 kV and lower, the control cabinet can be integrated with the Operating mechanism cabinet of 1-phase or 3-phase circuit breakers.

- The common control cabinet is made of aluminum alloy or stainless steel (Inox 304), the cabinet has a minimum thickness of 2 mm. The control cabinet must withstand severe weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets. Cabinet door designed with latch lock and key lock, gaskets have long service life in outdoor environment conditions. It is recommended to install the control cabinet at the position nearest to phase B. The control and protection circuits linking the control cabinets with the operation mechansim cabinets in the phases are recommended to use specialized cables and jacks manufactured by the manufacturer and supplied synchronously with the circuit breaker.

- Circuit breaker control circuit using 220VDC power supply, including:

+ 2 trip circuit working at 220VDC voltage with permissible voltage deviation (+10%; -30%) provided by 2 independent sources;

+ 1 closed circuit working at 220VDC voltage with permissible voltage deviation (+10%; -25 %).

+ The heating and lighting circuits in the cabinet use 220VAC power with voltage deviation (+10%; - 15 %).

- Equip the following equipment at the local control cabinet of the circuit breaker:

+ Switch selection of Local/Remote position (in which: Local: selects local operation; Remote: selects remote operation).

+ Control switch On/Off operation in local: can use the self-return switch type or the “OPEN/CLOSE” push buttons.

- The secondary terminal clamps must be able to expand at locations with multiple connections to prevent connecting multiple conductors in the same location. The number of terminal clamps for spare at least 20% of the connected terminal. Terminal for closing circuit or tripping circuit not located close to AC or DC power terminal. The power supply cable is independent of the control cable.

- The control cabinet must be equipped with auxiliary relays, time relays, magnetic starters, and overcurrent and overvoltage protection circuits for motors, which should be placed in the common control cabinet to avoid damage caused by vibrations arising from operation mechanism when switching circuit breakers.

- Inside cabinet have common grounding copper rod with pre-drilled holes and attached nut bolts for grounding connection.

- The control cabinet must be equipped with the following systems: automatic heating, automatic lighting by led lights, AC sockets, MCB with auxiliary contacts.

- Operational requirements

- Spring mechanism can be charged by manual and electric. In normal operation, the electric spring recharge shall begin immediately and automatically when the end of a closing cycle, the spring recharging time shall not exceed 15 second. The process of storing the spring is not interrupted until the spring is fully charged. When the closing spring is not fully charged, the lock cannot close the circuit breaker.

- Spring charge motor uses a DC voltage of 220 VDC and is recommended to use an additional 220 VAC source (depending on actual conditions at the substation). The spring charge motor must operate normally with the supply voltage deviates within (+10%; -15%) from the rated value of the DC or AC power supply. There is an overcurrent and overload protection circuit for the motor.

- The circuit breaker must have a device to prevent simultaneous remote control with local control. There is protective circuit for anti-pumping, operation locking circuits (lockout), signals (alarm); signal circuit of error spring stored and locks the circuit of the spring motor, non-synchronous phases protection circuit, electrical interlock circuit when one of the following cases occurs: SF6 gas pressure drops below rated value, spring is not fully charged, tripping circuit damage.

- Cable requirements:

- AC and DC power cables are provided with separate cables, cross-section not less than 2.5 mm2. Control and signal cables use cables suitable for the manufacturer's circuit breakers, with a cross section of not less than 1.5 mm2. Secondary cables used are waterproof, fireproof, the shielded to interference-proof and copper cores with high quality, many fibers. For the single-phase circuit breakers, the connection between operating mechanism cabinets and common control cabinet should be use cable with Plug-in prefabricated jacks which supplied synchronously with circuit breakers manufacturer.

### Installation arrangement

- Circuit breakers shall be suitably designed for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm. The steel for the support is highly durable, withstands the loads of the circuit breaker and meets the requirements of the circuit breaker manufacturer. The cross-section of the support structures must be large enough to reduce vibration when operating the circuit breaker. Steel parts (support structures, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 with coating thickness not less than 80 µm , the current standards for dip galvanizing , bolts and nuts.

- In case the operating mechanism cabinet (control cabinet) of the circuit breaker is designed and installed with a height of more than 1.3 m above the ground, it must be attached with operator’s stand.

- Non-electric metal structures parts, equipment enclosures, operation mechanism cabinet enclosures, control cabinets enclosures etc. of the circuit breaker must be directly earthed into the common grounding system of substation at the installation site. The grounding point of the circuit breaker must have the symbol "grounding", located at a convenient location to connect the grounding system of the substation. The cabinet enclosures and the cabinet door of the operation cabinet and control cabinet are grounded with multi-strand copper wire with insulated sheath, the cross-section of the copper wire is not less than 1.5 mm2.

- Circuit breaker must be attached to the Parameter Table and the circuit breaker label is made of aluminum alloy or stainless steel (Inox 304) , fully showing the main parameters of the circuit breaker according to IEC 62271-100. The data in the Parameter Table and the circuit breaker label must be highly durable, not lose color and always read clearly during the operation of the circuit breaker.

- During the installation process, must strictly follow the installation process, install the circuit breaker according to the instructions of the manufacturer; use materials and accessories for CB to ensure quality, in accordance with the requirements of the manufacturer. The entire process of installing and setting the circuit breaker must be carried out under the supervision of a specialist from the manufacturer or a supervisor must have a certificate issued or authorized by the manufacturer. In the record of acceptance of the installation of the circuit breaker or the test of setting a new circuit breaker must be signed by the qualified supervisor mentioned above.

### Accessories of circuit breaker

The circuit breaker must be equipped with the following accessories:

- The Terminal suitable for connecting conductors/bars and circuit breaker terminals are made of aluminum alloy .

- Stainless steel bolts, nuts, washers respectively.

- The structure and support of the CB.

- Contact grease, lubricating grease, specialized paper for cleaning the contact surface, spare rubber gaskets, SF 6 gas are enough for the first gas charge for the circuit breaker at the site.

- Specialized tools specific to CB: installation tools, manual tools for the CB and for the operating mechanism storage unit.

### Other requirements for circuit breaker

- Circuit breaker is new 100%, no defects; certified origin (CO) is clear, legal; CB has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- The manufacturer undertakes to warrant the equipment according to current commercial regulations as well as regulations on ensuring the technical life of the equipment stated in “Item (3) Equipment life requirements” of this Regulation.

### Equipment life requirements

The reliability requirements as well as the life requirements of the circuit breakers are determined with the following minimum conditions:

- The number of safe mechanical switching operations is not less than 10000 times (equivalent to class M2).

- Number of times of switching operations at rated current is not less than 2500 times.

- The number of times O-t-CO-ta-CO rated cycle operation is not less than 500 times.

- Number tripping for breaking times corresponding to the value of 50% of the rated short-circuit breaking current is not less than 30 times.

- Number tripping for breaking times corresponding to the value of 100% of the rated short-circuit breaking current is not less than 10 times.

### Requirements for testing for circuit breaker

### General requirements for test documentation:

Supplied circuit breakers shall be accompanied by adequate documentation demonstrating ability to meet the above technical specifications as well as IEC standards specified for each component of the equipment.

Manufacturer and /or supplier of circuit breaker is responsible for providing a full records, Type test, factory test (Routine test) demonstrating the ability to meet working requirements for supplied equipment, in which:

a. The type test report shall be issued by the independent testing laboratories which are member of STL organization (Shorting Testing Liasion).

b. The Routine Test reports are made and issued by the circuit breaker manufacturer.

### Test requirements for circuit breakers:

The design, manufacture and testing of circuit breakers shall comply with IEC 62271 - 100 or higher. The manufacturer shall provide the following test documents:

a. Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports.

During the procurement of new circuit breakers, it is required to provide documents demonstrating compliance with the following 7 types of tests in accordance with IEC 62271-100:

- Dielectric test.

- Measurement of the resistance of the main circuit.

- Temperature rise tests.

- Short-time withstand current and peak withstand current tests.

- Short-circuits current making and breaking tests

- Additional tests on auxiliary and control circuits.

- Mechanical operation tests at ambient temperature (class M1).

For the following cases:

- The 500 kV, 220 kV, 110 kV circuit breakers have special requirements on switching overvoltage and rate of rise of the transient recovery voltage.

- Special cases shall be decided by competent persons.

The manufacturer may be required to provide documents proving partial or total compliance with the following 11 types of tests according to IEC 62271-100:

- Test to Verification of the degree of protection.

- Tightness tests.

- Humidity tests.

- Extend mechanical endurance tests on circuit-breakers for special service condition, class M2 rating;

- Low and high temperature tests;

- Critical current tests;

- Short line fault tests;

- Out - of - phase making and breaking tests

- Single-phase fault test.

- Switching of shunt reactors and motors as specified IEC 612271-110

- Capacitive current switching tests

b. Routine test:

The manufacturer must provide documents of six routine tests according to IEC 62271-100 standards as following:

- Dielectric test on the main circuit.

- Tests on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Tightness test.

- Design and visual checks.

- Mechanical operating tests.

The manufacturer is responsible for providing a records, routine test results of the above tests.

### Requirements for transporting of circuit breaker

- Circuit breaker’s components is possible to remove or packing with a table listing the number of equipment and material supplies in each package for easily stored, transported by machine or manually, allowing re-installation and operation easily.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration, the impact of sea water, thunderstorms as well as other environmental influences.

### Requirements for documents of circuit breaker

It is the responsibility of the manufacturer to provide complete documentation of the following:

- Table of required parameters for circuit breakers.

- Drawings describing the structure, dimensions and cross-sections of the main components of the equipment: circuit breakers, poles, operation mechanism cabinets, control cabinets; quantity, drawing, specification of circuit breaker gaskets and circuit breaker accessories.

- Principle drawing and internal connection of control cabinet, operation mechanism cabinet.

- Installation instructions drawings (including Support Structure drawings).

- Test records meet the requirements of IEC specification and standards.

- Certificates of quality management system, origin of products and accessories.

- Manufacturer's catalog and regulation of SF6 gas applicable in circuit breakers.

- The documentation, recommendations for implementation: packaging, transportation, installation, operation, inspection, maintenance of equipment and accessories, overhaul, periodic testing, reinforcement testing (such as frequency performance, content of work) ; common defects and how to deal with common failures.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for circuit breakers

- Items not mentioned in the "Regulations on basic technical characteristics of 220 kV, 110 kV, circuit breakers on the power transmission grid" shall be applied according to the technical regulations of EVN, EVNNPT, TCVN standards, IEC or equivalent standard.

### Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker

- The Bidder must to appoint at least 01 Circuit Breaker Professional of for Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker during install Circuit Breakers this package at outside (at 500kV Quynh Luu substation). Circuit Breaker Professional  had to the manufacturer's training certificate or provide the authorization supervise for Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker.

- Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker according to 2878/EVNNPT-KT ngày 17/08/2018 doccument

### Basic Data of 500 kV Circuit Breaker and 220 kV Circuit Breaker:

- Refer to Technical Data Sheet to have data of 500 kV Circuit Breaker and 220kV Circuit Breaker.

## 35kV Circuit breaker

### General Requirement:

- Comply with the Technical standards of 35kV outdoor circuit breakers in National Electricity of Vietnam issued together with the Decision No. 272/QD-EVN dated April 24, 2019 of Electricity of Vietnam,

### 35kV Circuit Breaker:

- Circuit breakers capable of switching circuits in normal operation and breaking circuits in abnormal or fault operating modes of the grid with rated voltage of 35kV.

- Circuit breaker  has 3 phase common transmission, each phase has 01 cutting chamber, using vacuum or SF6 gas to extinguish the arc, suitable for outdoor installation and operation.

- Circuit breaker is designed and tested to IEC 62271-100 or equivalent and to the requirements given in the specification sheet (datasheet fo 35kV Circuit breaker).

- Bushing Insulators of circuit breakers must be made in accordance with environmental conditions and specifications, so in the technical requirements table (datasheet for 35kV Circuit breaker).

- Circuit breakers shall be designed so that defective/damaged contact chambers and other components can be inspected and replaced quickly and easily.

- The circuit breaker design must be safe if there is an overvoltage phenomenon when switching or Trip when short circuit.

- For SF6 gas-insulated and arc-extinguished circuit breakers, the product meets the requirements for the tightness of the SF6 gas system with gas leakage ≤ 0.5%/year of the entire gas volume.

- SF6 gas or other insulating and arc-extinguishing materials shall meet the detailed requirements given in IEC 60376. All materials used in the construction of the SF6 gas circuit breaker must be suitable for working conditions in the SF6 atmosphere and the decomposition products of SF6. Circuit breaker shall be able to withstand the maximum pressure it can generate during operation without gas leakage or deformation damage.

- The gas system of the cutting chamber must have a gas pressure gauge and a monitoring device to detect SF6 leaks at two levels. Level 1 must signal and level 2 must lock the circuit breaker operating circuit (lockout).

- The insulator of the circuit breaker post shall be manufactured according to IEC 62155 or equivalent. Porcelain insulators must have thermal, mechanical, electrical insulation, and operate in accordance with environmental conditions and specifications stated in the technical requirements table (datasheet for 35kV Circuit breaker).

### Drive cabinet of 35kV Circuit breaker:

### Actuator:

- Each circuit breaker shall be equipped with an on-site drive cabinet containing the operating mechanism, corresponding controls and relays, switches, clamps for control cables and other auxiliary equipment.

- The drive cabinet housing can be made of materials such as aluminum alloy, stainless steel and the surface of the enclosure can be painted in accordance with the general specification; the drive cabinet has a minimum tightness level of IP55.

- The actuator and associated equipment shall be capable of withstanding IEC 62271-100 operating forces and have a safety switching frequency of at least 10,000 times.

- Equipped with open/close status indicator of the breaker for easy identification without having to open the actuator door.

- Equip the following equipment at local control cabinet:

- Operation position selection lock of CB Local/Remote (In there: Local: local CB operation selection; Remote: remote CB operation selection).

- Locking on/off local operation CB: Can use self-return switch or Open/close buttons;

- Count of times Trip/Close of CB;

- Auxiliary contact system and stroke switch to control the accumulator motor and signal the charge state of the spring;

- There is an indicator of the status of spring storage: symbol / or text to identify the closed circuit spring state of the CB that has been charged and not charged.

- The second row of clamps must be extended at locations with multiple connections to avoid connecting multiple cables in one location. There is a minimum of 20% redundancy in connection clamp rows. The clamp row contacts must be designed firmly, not rusting during operation.

- Inside the control cabinet, there must be a common grounding rod in copper, with positions to connect to the ground

### Operational requirements:

- Spring actuator can be stored manually or electrically automatically. In the normal operating mode, the electric spring recharge shall begin immediately and automatically with the end of a closing cycle, the spring charge time shall not exceed 15s. The process of storing the spring is not interrupted until the spring is fully charged. When the closing spring is not fully charged, the lock cannot close the circuit breaker.

- Spring-loaded motor uses 220VDC DC power supply.

- The CB shall have a mechanism to prevent simultaneous remote control with local control. There must be full circuits: Not in-phase (for single-phase transmission CB), anti-switching many times continuously, lockout, alarm circuits; There is a fault signal circuit of the accumulator spring mechanism and a lock of the stored spring motor circuit when there is a mechanical fault

### Installation arrangement:

- The CB shall be suitable for direct mounting on a hot-dip galvanized steel rack with a coating thickness ≥ 80 µm.

- In case the transmission cabinet (control cabinet) of the circuit breaker is designed and installed with a height of more than 1.3 m above the ground, it must be accompanied by an operating stand.

- Equipment must be equipped with details, grounding positions at all non-electrical steel structural parts, equipment cabinets, drive cabinets, etc. to connect to the grounding system of the substation

### Test requirements:

### Routine test report:

- 35kV circuit breakers shall be routine tested to IEC 62271-100 or equivalent including the following major items:

- Design and visual check;

- Dielectric test on the main circuit;

- Test on auxiliary and control circuit;

- Measurement of the resistance of the main circuit;

- Tightness test;

- Meachanical operating test

### Type test:

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports.

- Copies of the type test report issued by the internationally recognized independent testing laboratory which are members of STL (Short-Circuit Testing Liaison) organization shall be submitted with the Tender by IEC 62271-100 including the following major items:

- Dielectric tests;

- Measurement of the resistance of the main circuit;

- Temperature-rise test;

- Short-time withstand current and peak withstand current tests;

- Additional test on auxilliary and control circuits

- Mechanical operation test at ambient temperature (Class M1);

- Test circuits for short-circuit making and breaking tests.

- In addition, depending on the requirements of the installation location and the purpose of circuit breaker, it is possible to add optional items according to IEC 62271-100 including the following major items:

- Verification of the degree of protection;

- Tightness tests (Controlled, sealed or closed pressure systems);

- Electromagnetic compatibility (EMC) tests;

- Extend mechanical endurance tests on circuit-breakers for special service condition;

- Short line fault tests;

- Out - of - phase making and breaking tests

Note: All tests have fully demonstrated the responsiveness of the equipment offered by bidder. The contractor may be rejected if does not meet the above requirements.

### Requirements for accessories of circuit breaker

- Equipment included with the 35kV circuit breaker includes:

- HV terminal clamps are suitable for connecting conductors/bars and circuit breaker HV terminal clamps.

- Bolts clamps are suitable for connecting conductors/bars connection with ground;

- Bolts, nuts of CB;

- Steel structure for CB.

- Contact grease, lubricating grease, specialized paper for cleaning contact surfaces, rubber gaskets

### Drawings and description

- The equipment shall provide the following drawings and technical documentation:

- Drawing depicting the general structure of a 35kV circuit breaker;

- Principle drawing and internal connection of control and transmission cabinets;

- Installation instructions drawings (including operating stand, Steel structure for CB drawings).

- Documentation for installation, operation, repair and maintenance of equipment and accessories;

- Documents on recommended inspection, testing, maintenance, overhaul, how to handle common malfunctions;

- Test report, CO, CQ…

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for circuit breaker

- Circuit breaker is new 100%, no defects; certified origin (CO) is clear, legal; CB has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- Circuit breaker meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts) must be hot-dip galvanized according to TCVN 5408:2007, current equivalent standards for dip galvanizing.

- During shipping, individual parts may be unpacked and unpacked and the number of supplies in each package must be listed.

### Basic Data of 35kV Circuit Breaker:

- Refer to Technical Data Sheet to have data of 35kV Circuit Breaker.

## 500kV, 220kV, 110 kV Disconnectors and Earthing Switches

### General

- Comply with the Technical standards of 500kV and 220kV, 110kV outdoor Disconnectors and Earthing Switches in Decision No. 1676/QD-EVNNPT dated August 24, 2025 of National Power Transmission Corporation.

### Definition of disconnectors for power transmission grid

- The disconnector for the power transmission grid is a device capable of participating in the high-voltage switching circuit in normal operating mode, only performing switching on the high-voltage circuit when there is no current or a smaller current the equipment's tolerance, creating a safe distance between live and non-energized parts. Disconnector on the power transmission grid must meet the durability of the climatic and environmental conditions in Vietnam: tropical, suitable for the environmental conditions of installation and operation of the substation.

- The basic standards for applying the design, manufacture and testing of disconnectors in power transmission grid are IEC 62271-102 and IEC 62271-1.

- For disconnectors with integrated electrical circuit breaking function, IEC 62271-108 standard is additionally applied.

### General requirements on standards and environment

- All disconnector’s equipments on the power transmission grid that is manufactured and installed must meet Vietnamese regulations, standards, electricity industry standards, IEC/IEEE standards and be able to work stably long term under demanding working conditions, including Vietnam's natural climatic and environmental conditions.

- Environment conditions:

| Parameter | Request value |
| --- | --- |
| Altitude above sea level | : no more than 1000 m |
| Climatic condition | : Tropical |
| Maximum air temperature | : 45°C |
| Minimum air temperature | : 0°C |
| Average air temperature | : 25°C |
| Maximum humidity | : 100% |
| Average humidity | : 85% |
| Creepage distance | : 25mm/kV |
| Seismic factor | : 0.15g |

- Depending on the natural conditions of the equipment installation location, as determined in QCVN 02:2009/BXD, the above environmental condition values may be changed to suit the actual requirements to be applied.

### General requirements from power transmission systems

Table 1

| Parameter | Unit | Request value |  |  |
| --- | --- | --- | --- | --- |
| Normal Voltage | kV | 500 | 220 | 110 |
| Rated Frequency | Hz | 50 |  |  |
| Max operating voltage | kV | 550 | 242 | 121 |
| Min operating voltage | kV | 450 | 198 | 99 |
| Connection diagram |  | 3 phase, 3 wire |  |  |
| Method of neutral grounding |  | Directly grounded |  |  |
| Grounding touching coefficient of transmission grid |  | ≤ 1,4 |  |  |

### Quality certificate requirements:

- The manufacturer must have a certificate of the quality management system (ISO 9001:2015 or equivalent, still valid) applied to the production of the disconnector's component parts. The manufacturer must have a factory testing laboratory with certified testing equipments.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, labels for commercial and technical, etc.

### Requirements for component parts of disconnector

### Disconnector

- 500 kV, 220 kV, 110kV disconnectors installed on the power transmission grid are three phases or single phase, designed and manufactured in accordance with IEC 62271-102 standards so that they can be installed outside under the operating conditions of Vietnam's power transmission system. In addition to the IEC 62271-102 standard, the disconnector must meet the IEC 62271-1, IEC 60060 standards and must meet the requirements for insulation durable and temperature rise during long-term operation.

- Disconnectors are designed and manufactured to ensure safe operation under normal as well as fault conditions, to withstand atmospheric overvoltages, overvoltage phenomenon occurs when switching operation. The technical voltage requirements for disconnectors are clearly stated in technical datasheet.

- The disconnector shall meet the long-term operating current and short-circuit current requirements specified in technical datasheet without exceeding the permissible operating temperature limits specified in IEC 62271-102.

- Disconnector must be properly designed and manufactured so that it cannot be opened or closed automatically by external forces. The safe distance for disconnectors in static position (static state) is specified in technical datasheet. In case of operation, if the distances between parts of the disconnector do not meet the safe distances in the static state, the equipment must ensure the insulation ability to withstand the power frequency voltage meets the voltage values for disconnectors equipped with earthing switches specified in technical datasheet.

- Disconnector must be properly designed and manufactured to enable easy inspection and prompt replacement of defective/damaged contacts and other parts. After assembly, the parts that make up the disconnector and the bracket must not create holes for birds to nest, which cause problems that affect the life of disconnector.

- The components of the disconnector must be designed and manufactured so that during operation under environmental conditions in the substation, overheating must not occur and must meet the requirements for temperature rise of the components parts of the disconnector specified in the standards IEC 62271-1:2017 and IEC 60137:2017.

- Disconnector with voltage levels of 220 kV and 110 kV are horizontal opening types. Depending on the area for safe arrangement of switching equipment in the substation, the 500 kV voltage level disconnector can be applied as vertical opening type. To save space in the substation, 500 kV voltage level disconnector are often applied as vertical break, knee type. The disconnector can be operated by electric motor and/or by hand crank.

### Earthing switch

- The earthing switch attached to the disconnector is manufactured in accordance with IEC 62271-102 standards so that it can be installed outdoors under the operating conditions of Vietnam's power transmission system.

- Depending on the installation location and working requirements, each disconnector may be equipped 01 earthing switch or 02 earthing switch or without earthing switch. The earthing switch must meet the short-circuit withstand current requirements specified in technical datasheet without exceeding the permissible operating temperature limits as specified in standard IEC 62271-102.

- Disconnectors for transmission line with a length greater than 50 km or transmission line with multiple circuits operating in parallel, the earthing switch must be capable of switching electrostatically induced capacitive currents and electromagnetically induced currents with the values specified in Table 2 to meet the regulation according to IEC 62271-102.

- Earthing switch must be properly designed and manufactured so that it cannot be opened or closed automatically by external forces.

- The moving part of the earthing switch must be grounded to the disconnectors base by a soft copper wire or copper foil with a cross-section of not less than 50 mm2, ensuring it does not break or hinder the operation of earthing switch.

### Poles post of disconnector

- Pole post (supporting porcelain post) of disconnector must be made of non-assembled cylindrical porcelain, canopy circle, brown color according to IEC 60273 or equivalent. Porcelain must have thermal, mechanical and electrical durability, operate in accordance with the environmental conditions and technical characteristics listed in technical datasheet.

- Insulation porcelain of disconnector are manufactured to ensure that the distances from live parts to earth and between live parts comply with the requirements detailed in technical datasheet.

- Insulation porcelain of disconnector must be able to withstand the impact loads specified in detail in technical datasheet.

- Connection between of pole post and disconnector’s blade must be linked by bolts or welding to ensure no heat during long-term operation.

### Operating mechanism

- Operating mechanism and associated devices must be able to withstand impact forces according to IEC 62271-102 standard. Operating mechanism of disconnector must have safe mechanical switching at least 2000 times (equivalent to class M1). Operating mechanism of earthing switch must have safe mechanical switching at least 1000 times (equivalent to class M0).

- The contacts of the disconnector and earthing switch must be made of materials such as copper, copper alloy or silver/nickel plated aluminum alloy.

- The drive mechanism are made of non-corrosive, high-strength metal materials without rust, with an anti-skid lock.

- The drive motor circuit of the disconnector uses 220 VDC power source with voltage deviation (+10%; -15%) of rate voltage value. Motors must be equipped with overcurrent and overload protection.

### Drive mechanism cabinet, control cabinet

- Control cabinet can be integrated with the drive mechanism cabinet.

- Each disconnector must be equipped with local drive mechanism cabinet including the drive mechanism (can be use one drive mechanism cabinet for three-phase disconnectors), control lock, corresponding relays and switches, auxiliary contacts, limit contacts, clamps for control cables, LED lighting, drying resistors, power sockets, aptomat with auxiliary contacts, ventilation holes and other auxiliary equipment.

- Enclosure of mechanism cabinets and control cabinets can be made of aluminum alloy or stainless steel (304 stainless steel) or galvanized steel and the cabinet surface can be painted accordance to general technical requirements. The cabinet has a minimum thickness of 2 mm. The control cabinet must withstand extreme weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets.

- The mechanism cabinets is installed steady on a bracket structures to ensure not excessive vibration or abnormal phenomenon when operating disconnector and earthing switch, which can affect the life of disconnector.

- The mechanism cabinets of disconnector and earthing switch must be placed in a suitable position for does not affect the operator by arcing, and the operator can easily observe the movement contact during operation.

- The mechanism cabinets of disconnector and earthing switch equipped with the following parts:

- Selection switch of Local/Remote for position operating disconnector (in which: Local: select operate disconnector at local; Remote: select operate disconnector at remote).

- Close/Open switch for operating disconnector at local: can use self-return switching or "Open/Close" push buttons.

- Overcurrent and overload protection relays for the motor should be placed in the control cabinet.

- Auxiliary contact system and limit switch to control motor operation. Each DS/ES is equipped with auxiliary contact according to the status of the main DS/ES contact.

- The wiring terminals and connection terminals of the auxiliary contact block and limit switch in the mechanism/control cabinet must be made of stainless steel or metal treated to prevent rust. The secondary terminal must be able to expand at locations with many connections to limit the connection of many wires in same location. The number and technical requirements of auxiliary contacts must ensure compliance with the requirements stated in technical datasheet.

- The disconnector control circuit uses a 220 VDC power source with permissible voltage deviation (+10%; -15%).

- The drying and lighting circuits in the cabinet use a 220VAC power source with permissible voltage deviation (+10%; -15%).

- Inside control cabinet have common grounding copper rod with pre-drilled holes and attached nut bolts for grounding connection.

### Operation requirements

- The disconnector and earthing switch can be operated by manual and/or electrical to control close/open.

- Motor uses a 220 VDC voltage source.

- The disconnector must have a mechanism to prevent control in remote mode and local mode at the same time. Must have all circuits: electrical interlock circuit (interlock); motor error signal circuit; motor protection circuit; Non-synchronous signal circuit (for single-phase diaconnector/earthing switch), AC and DC power supply warning circuit for drying, lighting, motor, control circuit, ...

- DS/ES equipped with electrical and mechanical interlock (prohibited control to closing ES if DS side is energized) to prevent unwanted misoperation, ensure the safety of operators and equipment under operating conditions. In addition, the mechanical interlocks must operate reliably to avoid mechanical jamming when operate at the permissible electrical interlocking conditions.

- Operating mechanism force for DS or ES must not exceed 250N if only one rotation is required and not exceed 120N if multiple rotations are required (in case of manual operation) according to IEC 62271 -102.

### Requirement of secondary cable

- AC and DC power cables are provided with separate cables, cross-section not less than 2.5 mm2. Control and signal cables with a cross-section not less than 1.5 mm2. Secondary cables used copper cable with high quality, many fibers which water-resistant, fire-resistant, and the shielded to interference-proof.

### Installation arrangement

- Disconnector shall be suitably designed for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- The steel for the support is highly durable, withstands the loads of the disconnector and meets the requirements of the disconnector manufacturer. The cross-section of the support structures must be large enough to ensure not excessive vibration or abnormal phenomenon when operating disconnector and earthing switch, which cause problems that affect the life of disconnector.

- Steel parts (support structures, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 with coating thickness not less than 80 µm, the current standards for dip galvanizing, bolts and nuts.

- In case the operating mechanism cabinet (control cabinet) of the disconnector is designed and installed with a height of more than 1.3 m above the ground, it must be attached with operator’s stand.

- Non-electric metal structures parts, equipment enclosures, operation mechansim cabinet enclosures, control cabinets enclosures, etc. of the disconnector must be directly earthed into the common grounding system of substation. The grounding point of the disconnector must have the symbol "grounding", located at a convenient location to connect the grounding system of the substation. The cabinet enclosures and cabinet door are grounded with multi-strand copper wire with insulated sheath, the cross-section of the copper wire is not less than 1.5 mm2.

- Disconnector must be attached to the Parameter Table and the disconnector label is made of aluminum alloy or stainless steel (Inox 304), fully showing the main parameters of the disconnector according to IEC 62271-102. The data in the Parameter Table and the circuit breaker label must be highly durable, not lose color and always read clearly during the operation of the disconnector.

- During the installation process, must strictly follow the installation process, setting the disconnector according to the instructions of the manufacturer; use materials and accessories for DS to ensure quality, in accordance with the requirements of the manufacturer. The entire process of installing the disconnector must be carried out following sequence specified by the manufacturer.

### Accessories:

Disconnector must be equipped with the following accessories:

- The terminal clamp suitable for connecting conductors/bars and terminal at HV side are made of aluminum alloy.

- Bolts and nuts made of stainless steel or hot-dip galvanized steel with a coating surface of not less than 80 μm, washers and anti-fall rings are included respectively.

- Bolts suitable for copper wire/grounding conductor.

- Structure and support of disconnector.

- Joint grease, lubricating grease, specialized paper for cleaning the contact surface.

- Specialized tools specific to disconnector: installation tools, manual tools for disconnector and earthing switch (Hand-wheel/operated lever).

### Other requirements

- Disconnector is new 100%, no defects;

- The manufacturer must to commit the certified origin, certificate quality of goods, attach relevant documents and warranty the equipment according to current regulations commercial compliance as well as regulations on ensuring the technical life of equipment stated in item d - (The life requirements) of this Regulation.

### Basic technical parameters of disconnector

- Table 2 (Refer to Technical Data Sheet to have data of 500kV, 220kV Disconnector and Earthing switch)

### The life requirements

The reliability as well as the life requirements of the disconnector are determined with the following minimum conditions:

- The number of safe mechanical switching operations is not less than 2000 times (equivalent to class M1) for disconnector.

- The number of safe mechanical switching operations is not less than 1000 times (equivalent to class M0) for earthing switch.

- Safe operating time before overhaul: at least 10 years or according to class M1 for disconnector, at least 10 years or according to class M0 for earthing switch (depending on condition comes first).

- Operating life for disconnector: minimum 25 years.

### Requirements for testing

##### The manufacturer is responsible for providing complete documentation of the following:

- Supplied disconnectors shall be accompanied by adequate documentation demonstrating ability to meet the above technical specifications as well as IEC standards specified for each component of the equipment.

- Manufacturer and/or supplier of disconnectors is responsible for providing a full records, Type test, factory test (Routine test) demonstrating the ability to meet working requirements for supplied equipment, in which:

- The type test report shall be issued, or witness, or confirmed by the independent testing laboratories which are member of STL organization (Shorting Testing Liasion).

- The Routine Test reports are made and issued by the disconnector manufacturer.

##### Test requirements for disconnector:

Design, manufacture and testing comply with IEC 62271-102. The manufacturer must provide the following test documents:

Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

Disconnectors have voltage level of 500 kV, 220kV, 110kV that already commonly used types on the power transmission grid in Vietnam, it is required to provide documents of five type tests according to IEC 62271-102 standards as following:

- Dielectric tests.

- Measurement of the resistance of the main circuits.

- Continuous Current Test.

- Short time withstand current and peak withstand current tests.

- Mechanical endurance test.

For the following cases:

- The 500 kV, 220 kV, 110 kV disconnectors have special requirements on installation location or purpose.

- Special cases shall be decided by competent persons.

Then maybe require the manufacturer provide documents for proving partial or total compliance with the following 15 types tests according to IEC 62271-102

| No. | Test item | Condition | Equipment |  |
| --- | --- | --- | --- | --- |
|  |  |  | DS | ES |
| 1 | Test to verify the degrees of protection of enclosures | According to IP | x | x |
| 2 | Radio interference voltage RIV test | Ur>Umax | x | x |
| 3 | Tightness tests | the systems are controlled, sealed, sealed pressure | x | x |
| 4 | EMC tests |  | x | x |
| 5 | Additional tests on auxiliary and control circuits | With auxiliary and control circuits | x | x |
| 6 | Test to prove the short-circuit making performance of earthing switches | For E1, E2 type |  | x |
| 7 | Contact zone test |  | x | x |
| 8 | Operation during application of rated static mechanical terminal load |  | x | x |
| 9 | Extended mechanical endurance tests | For M1, M2 type | x | x |
| 10 | Testing on mechanical interlocking devices | With interlocking | x | x |
| 11 | Low and high temperature tests | If the ambient temperature is greater than 40oC or less than -5oC | x | x |
| 12 | Tests to verify the proper functioning of the position-indicating device | With the position-indicating device | x | x |
| 13 | Bus transfer current switching tests | Bus transfer current switching ability | x | x |
| 14 | Induced current switching tests | A or B type |  | x |
| 15 | Bus-charging current switching tests | Bus-charging current switching ability | x |  |

Routine test

The manufacturer must provide documents of six routine tests according to IEC 62271-102 standards as following:

- Dielectric test on the main circuit.

- Tests on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Design and visual checks.

- Mechanical operating tests.

- Verification of earthing function (applies to DSs equipped with ES).

The manufacturer is responsible for providing a full records, routine test results of the above tests.

### Requirements for transporting of disconnector:

- Disconnector’s components is possible to remove or packing with a table listing the number of equipment and material supplies in each package for easily stored, transported by machine or manually, allowing re-installation and operation easily.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration, the impact of sea water, thunderstorms as well as other environmental influences.

### Requirements for documents of disconnector:

The manufacturer is responsible for providing complete documentation of the following:

- Table of required parameters for disconnector.

- Drawings describing the structure, dimensions and cross-sections of the main components of the equipment: disconnector, main blade, earthing blade, poles, operation mechanism cabinets, control cabinets, HV terminal, supporting structure; quantity, drawing, specification of accessories.

- Principle drawing and internal connection of control cabinet, operation mechanism cabinet.

- Installation instructions drawings (including support structure drawings).

- Test records meet the requirements of specification and IEC standards.

- Certificates of quality management system, origin of products and accessories.

- The documentation, recommendations for implementation: packaging, transportation, installation, operation, inspection, maintenance of equipment and accessories, overhaul, periodic testing, reinforcement testing (such as frequency performance, content of work); common defects and how to deal with common failures.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for disconnector

Items not mentioned in the "Regulations on basic technical characteristics of 500 kV, 220 kV, 110kV disconnector on the power transmission grid" shall be applied according to the technical regulations of EVN, EVNNPT, TCVN standards, IEC or equivalent standard.

### Basic Data of 500kV, 220kV, 110kV Disconnector and Earthing switch

Refer to Technical Data Sheet to have data of 500kV, 220kV, 110kV Disconnector and Earthing switch.

## 35 kV Disconnectors and Earthing Switches

### General

Comply with the Technical standards of 35kV Disconnector and Earthing Switch in of Electricity of Vietnam issued together with the Decision No. 271/QĐ-EVN dated 24/07/2019 and No.91/QD-HDTV dated August 18, 2023

Disconnector switch is the type using three phases, outdoor installation, two column center break type, comply with standards IEC 62271-102. Disconnector switch is horizontal opening type, which can be operated by hand-wheel or electrical motor. The mechanical mechanism of the disconnector switches must be designed so that the disconnector switches cannot close or open itself by external impulses.

Earthing switch fitted with disconnector: 3-phase (corresponding to disconnector type), outdoor installation and comply with standards IEC 62271-102. The earthing switch can be operated by a lever, hand-wheel and electrical motor. The mechanical mechanism of the earthing switches must be designed so that the earthing switches cannot close or open itself by external impulses.

### Operating control cabinet

          - Operating mechanism

- The drive mechanism and associated equipment must be able to withstand the impact forces according to IEC 62271-102.

- Disconnector must be equipped with a local operating control cabinet containing the operating mechanism, control lock and corresponding relays, switches, clamps for control cables and other auxiliary equipment. Connection clapms and connection clamps of  auxiliary and position contact block in operating and drive cabinet must be made of stainless steel or stainless treated metal.

- Drive cabinet cover can be made of materials such as aluminum alloy, stainless steel or galvanized steel and can be painted on the surface of the enclosure in accordance with the general specification, thickness ≥ 2mm, drive control cabinet is mounted on sturdy supporting, weatherproof, protection class IP 55.

- Having open-close status indicator of disconnector and earthing switch for easy identification without opening the door of the cabinet.

- Equip the following equipment at the local control cabinet of the disconnector:

- Switch selection of LOCAL/REMOTE position (in which: Local: selects local operation; Remote: selects remote operation).

- Control switch On/Off operation in local: can use the self-return switch type or the “OPEN/CLOSE” push buttons.

- The auxiliary contact system and the limit switch contact to control the motor. Each disconnector/earthing switches is equipped with auxiliary contacts according to the state of the disconnector/earthing main contact.

          - Operational requirements

- Disconnector/earthing switches can operate on/off by manually and motor.

- Rate voltage of motor driver for DS and ES: 220VDC.

- DS/ES equipped with electrical and mechanical interlock to prevent unwanted misoperation, ensure the safety of operators and equipment under operating conditions.

### Installation arrangement

- Disconnector shall be designed to be suitable for direct mounting on hot-dip galvanized steel supports.

- Equipment must be equipped with details, grounding positions at all parts of non-charged steel structures, equipment cabinets, control cabinet,... to connect to the grounding system of substation.

### Requirements for testing

          - Factory test report:

Disconnector shall be factory tested in accordance with IEC 62271-102 or equivalent standard comprising the following main items:

- Design and visual checks.

- Dielectric test on the main circuit.

- Test on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Mechanical operating tests.

- Verification of earthing function.

          - Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 4.12. Required for list of type test reports.

The type test report shall be issued by the independent testing laboratories, including the following main items:

- Dielectric tests;

- Measurement of resistance of the main;

- Continuous current test;

- Short time withstand current and peak current withstand tests;

- Mechanical endurance test.

In addition, depending on the requirements of the installation location and the purpose of DS, it is possible to add optional items according to IEC 62271-102 including the following major items:

- Additional tests on auxiliary and control circuits

- Test to prove the short-circuit making performance of earthing switches

- Contact zone test

- Operation during application of rated static mechanical terminal load

- Extended mechanical endurance tests

- Testing on mechanical interlocking devices

- Low and high temperature tests

### Accessories of disconnector

- Terminal clamp for connecting.

- Bolts suitable for copper wire/grounding conductor.

- Bolts and nuts.

- Steel structure.

- Specialized join compound and paper for cleaning contact surfaces, rubber gaskets.

- Hand-wheel/operated lever to open and close DS and ES (if any) by manual.

### Drawings and description, Technical documents:

The equipment shall be provided with the following drawings and technical documentation:

- General structure drawings.

- Installation instructions drawings.

- Principle drawing and internal connection of control cabinet.

- Documentation for installation, operation, repair and maintenance of equipment, accessories.

- The documents recommend inspection, testing, maintenance, overhaul, how to handle common malfunctions and failures.

- Test reports and quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for DS

- Disconnector switch is new 100%, no defects; certified origin (CO) is clear, legal; has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- Disconnector switch meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts) must be hot-dip galvanized according to TCVN 5408:2007, current equivalent standards for dip galvanizing.

- Allow unpacking and packing of individual parts for transporting and there is a table listing the number of equipment and material supplies in each package.

### Basic Data of 35kV Disconnector and Earthing switch

- Refer to Technical Data Sheet to have data of 35kV Disconnector and Earthing switch.

Note:

- To ensure reliability of controlling, signaling and interlocking circuits of substation computerized control system  as well as reliability of busbar simulation circuit of busbar protections, the Disconnectors supplied shall be of high quality with best modern technology in design and manufacturing. The mechanical operating system shall be simple, easy of erection and adjustment, minimum of maintenance. The appropriate solutions shall be used to ensure the whole operating mechanism and transmission system of Disconnector and Earthing switches can operate securely, accurately and smoothly during all service lifetime.

- They shall be able to close and open whilst subjected to their rated mechanical terminal loads, plus wind loads acting on the equipment itself. HV main contacts shall securely lock in the closed position in such manner that they do not separate when subjected to the full rated short circuit current.

- Material of local control cubicle must be in Stainless Steel (Inox 304) or Aluminium Alloy (Al Mg3 H22).

- DS must be compliance with temperature-rise according to IEC 62271; IEC60137; vibration according to IEC 60068; IEC 60255; short circuit withstand according to IEC 62271-100,-1; insulation level according to IEC 62271; IEC 60137; IEC 60060.

- All Disconnector and Earthing switch (Designation HCB) from Siemens - India shall not be allowed for bid according to EVNNPT official document No. 3140/EVNNPT-KT+PC+ĐT+QLĐT+QLXD ngày 11/09/2019).

## 500kV Current Transformers

### General

Current Transformers of 500kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1819/QD-EVNNPT dated September 16, 2025 of EVNNPT.

The 500kV current transformer put into operation for power transmission grid is the type single phase, sealed type, Magnetic circuit and coil are placed on top of the current transformer, insulating oil, outdoor installation. Current transformer was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

Environment conditions:

- Climatic condition	: Tropical

- Average air temperature	: 25°C

- Maximum air temperature	: 45°C

- Minimum air temperature	: 0°C

- Average humidity	: 85%

- Maximum humidity	: 100%

- Seismic factor 	: 0.15g

- Creepage distance	: 25mm/kV

- Altitude above sea level	: < 1000 m

Requirements of the electrical system installing the current transformer

| Item | 500 kV system |
| --- | --- |
| Normal Voltage | 500 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 550 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |
| Grounding touching coefficient of transmission grid | ≤ 1.4 |

500kV current transformer designed and manufactured meet working conditions comply with standards: IEC 60071-1 (2011-03), IEC 60137 (2008-07), IEC 61869-1 (2007-10), IEC 61869-2 (2012-09), IEC 60529 (2001-02), IEC 60296 (2012-02), IEC 60422 (2013-01), IEC 60028 (1925), IEC 61850-7-3 (2010), IEC 61850-7-4 (2010-3), IEC 61850-7.20 (2009), IEC 61850-6 (2009-12),  IEC 61850-9-3 (2016-05), IEC 61869-9 (2016-4).

### Requirement temperature rise, insulation strength, short current circuit

The current transformer meet temperature rise requirement comply with standards: IEC 60137, IEC 61869-1, IEC 61869-2.

The current transformer meet insulation strength requirement comply with standards: IEC 60137 and IEC 61869-2.

The current transformer meet virbration requirement comply with IDC 60068-1 (2013-10).

The current transformer meet short current circuit requirement comply with standards IEC 61869-2.

### Requirements partial discharge, impulse discharge

Partial discharge values of current transformer (PD) comply table 3 IEC 61869-1

The Current transformer withstand multiple chopped multiple comply item 7.4.2 IEC 61869-1.

Switching impulse withstand overvoltage comply table 2, IEC 60060-1.

### Reliability requirements

Operation time until overhaul				: ≥ 10 years.

Total of operating time until to be replaced by a new CT	: ≥ 20 years.

### Requirements for component parts of current Transformers

          - Requirements for winding coils of current transformers

The coils are made of standard annealed copper at a temperature of 20 0C with resistivity no greater than [0.017241 (Ω.mm2/m); 0.15328(Ω.g/m)] comply with IEC 60028 (1925); Equivalent conductivity not less than 100% IACS.

The quality insulating material is consistent with the insulation strength and temperature of CT.

Insulation requirements between secondary windings: withstand voltage according to IEC 61869-2.

          - Requirements for magnetic cores of current transformers

The value of flexural dynamic force inflection point at rated frequency, when increased by 10% increases the excitation current by 50%.

Residual magnetic coefficient for protective coils does not exceed 10%.

          - Requirements for external insulation of current transformers

Materials: Non-assembled cylindrical porcelain (or composite), canopy circle, brown color.

Minimum creepage distance to meet the requirements of IEC 60815.

Porcelain must have thermal, mechanical and electrical durability.

Porcelain must be manufactured to meet the requirements of IEC 60137.

          - Requirements for secondary terminal box of current transformers

Material: Inox- 304 (stainless alloy), the thickness is not less than 02 mm.

Quantity of box: 01 with CT type with 6 secondary coils. For CT type with 8 secondary coils: 02 boxes are required.

Cover box with gasket, hinge, lock handle. Terminal clamps is suitable for O-ring terminals for wires with a cross section of not less than 4 mm2.

Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529.

Cable ends entering boxes and cabinets must have cable termination connectors sized to match the diameter of the cable to ensure cable end robustness and tightness for boxes and cabinets (when there is no cable, these holes must be covered with a screw cap).

          - Requirements for insulating oil

The oil used in CT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

The origin of oil, name, code and quantity of oil must be clearly stated in CT name plate.

CT must be tight without leaking oil. Oil level indicator, oil sampling valve, oil drain valve, oil replenishment position.

          - Requirements for solid insulate material

Solid insulate material must to be organic material  comply IEC 60455

          - Requirements for symbol of primary coil and secondary coil

Layout and symbols of primary coil and secondary coil comply item 6.03 IEC 61869-2

          - Requirements for clamping

The secondary wire must be fixed to the insulating board surface, the durability is definitely not loose when screwing.

### Requirements for Mechanical, power arc

CT is capable of withstanding static loads according to table 7, standard IEC 61869-1, test time according to item 7.4.5, test diagram according to table 12, standard IEC 61869-1.

The CT shall be able to withstand an internal arc in accordance with table 8, section 6.9, standard IEC 61869-1.

### Requirements for electromagnetic compatibility

The level of radio frequency disturbance voltage generated within the CT shall comply with section 6.11, standard IEC 61869-1 (2007).

The CT shall be capable of withstanding primary-to-secondary overvoltage with values ​​not exceeding the values ​​in table 9, standard IEC 61869-1 (2007).

### Requirements for earthing connection

The Grounding point must have a symbol according to IEC 60417, Arrangement convenient location for connection with earthing system.

### Requirements for accuracy class

For secondary windings having accuracy class 0.5: Current deviation, phase displacement measured at secondary windings not exceeding values ​​in table 201, standard IEC 61869-2).

For secondary winding with accuracy of class 5P: Current deviation, displacement measured at secondary winding, there is an error not exceeding value in table 205, standard IEC 61869-2).

### Requirements for specification sheet and label of current transformers

Material made of Inox 304 (stainless alloy). The handwriting is not faded during the life of current Transformers.

The content on the parameter table can fully display the main current Transformers parameters according to Item 6.13 at IEC 61869-2.

### Requirements for testing, checking, installing, maintenance

The Type Test, Special Test, Routine Test for current Transformers shall comply with requirements according to IEC 61869-1, IEC 61869-2 and submission all test report enclosed tested current Transformers. There must be test report for oil and current Transformers accessory testing.

Routine test  must to be content accreditation error of measurement coils in variance errors and phase angle errors

List of testing for CT comply to table 10, IEC 61869-2

Manufacturer supply Instructions documents for maintenance, repair, overhaul and test comply to IEC 61869-1. Instructions documents for Oil sampling and adding oils

### Requirements for transporting of current transformers

During transporting, it is do not allow separate dismantling and packaging the components.

Have solution to prevent moisture penetration and the impact of sea water.

### Requirements for documents of current transformers

- Manufacturer information, summary of current Transformers specifications, origin of current Transformers accessories, quality management certificate, certificate of quality of oil, certificate of quality of winding copper material, certificate of quality of magnetic core material.

- There are all test records.

- Instructions documents for transportation, installation, operation and maintenance of current Transformers.

- Generally drawings with dimensions, sectional drawings, structural drawings, current Transformers structural details drawings and accessories drawings.

- Guidelines for replacing or replenishing CT oil as well as standards for evaluating oil quality in operation and renewal.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

### Requirements for testing

The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

The Short-circuit withstand capability test must by one member of STL organization, have name in the list following: Intertek (ASTA, implemented before May 22, 2024)-UK; CESI-Italy; CPRI-India; ESEF ASEFA-France; JSTC-Japan; KEMA-Netherland; KERI-South Korea; PEHLA-Germany; SATS-Norway; STLNA-USA; VEIKI-Hungary; ZKU-Czech Republic.

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

The test items must be fully tested according to the standards specified in the Bidding documents or with standards equivalent to the specified standards.

Type test report:

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

The certificates required in according with IEC 60044-1, -2/IEC 61869-1, -2, including the following:

- Short-time current test;

- Temperature-rise test;

- Impulse voltage withstand test on primary terminals;

- Wet test for outdoor type transformers;

- Test for accuracy;

- Verification of the degree of protection by enclosures;

- Enclosure tightness at ambient temperature;

- Radio interference voltage measurement

Note: All tests have fully demonstrated the responsiveness of the equipment offered by bidder. The contractor may be rejected if does not meet the above requirements

- Routine Test

- Routine test is performed by the manufacturer on each product produced at the manufacturing facility. The routine tests are conducted in accordance with IEC 61869-1, -2 or TCVN 11845-2 or TCVN 7697-1 or equivalent standards, and include the following test items:

- Verification of markings

- Power - frequency withstand tests on primary terminals

- Power-frequency withstand test on secondary windings

- Power - frequency withstand test between sections

- Partial discharge measurement

- inter-turn overvoltage test

- Test for accuracy

- Check the housing for tightness at ambient temperature

- The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

### Requirements for accessories of current transformer

- The CT using insulating oil, a oil sampling device is required for periodic testing in operation; must have spare oil in service of repair.

- Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

### Other requirements for current transformer

- If secondary coil of CT manufacture by new technology, secondary circuit comply to IEC 61850-7-3 (2010); IEC 61850-7-4 (2010-03); IEC 61850-6.20 (2009); IEC 61850-6 (2009-12); IEC 61850-9-3 (2016-05); IEC 61869-9 (2016-04)

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

### Basic Data of 500kV Current Transformer

- Refer to Technical Data Sheet to have data of 500kV Current Transformer

Note: All 500kV CTs from GE shall not be eligible (EVNNPT has declared that all equipment 500kV CTs  from GE shall not be allowed for bid according to EVNNPT official document No. 465/EVNNPT-KT, dated 21/02/2022 and 1297/EVNNPT-KT+QLĐT, dated 15/04/2022.

## 220kV Current Transformers

### General

- Current Transformers of 220kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1819/QD-EVNNPT dated September 16, 2025 of EVNNPT.

- The 220kV current transformer put into operation for power transmission grid is the type single phase, sealed type, Magnetic circuit and coil are placed on top of the current transformer, insulating oil, outdoor installation. Current transformer was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition		: Tropical

- Maximum air temperature	: 45°C

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum humidity		: 100%

- Average humidity		: 85%

- Seismic factor 		: 0.15g

- Maximum wind velocity 		: 160 km/h

- Creepage distance		: 25mm/kV

- Requirements of the electrical system installing the current transformer

| Item | 220 kV system |
| --- | --- |
| Normal Voltage | 220 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 242 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |

- Current transformer designed and manufactured meet working conditions comply with standards: IEC 60044-1(2003-02); IEC 60815 (2008-10); IEC 60071 (2011-03); IEC 60137; (2008-07) IEC 61869-1 (2007-10); IEC 61869-2 (2012-09); IEC 60060 (2010-11); IEC 60529 (2001-02); IEC 60296 (2012-02); IEC 60422 (2013-01); IEC 60028 (1925).

### Requirement temperature rise, insulation strength, short current circuit

- The current transformer meet temperature rise requirement comply with standards: IEC 60137, IEC 61869-1, IEC 61869-2.

- The current transformer meet insulation strength requirement comply with standards: IEC 60137 and IEC 60060.

- The current transformer meet short current circuit requirement comply with standards: IEC 60044-1 and IEC 61869-2.

### Reliability requirements

- Operation time until overhaul: ≥ 8 years.

- Total of operating time until to be replaced by a new CT: ≥ 20 years.

### Requirements for component parts of current Transformers

- Requirements for winding coils of current transformers

- The coils are made of standard annealed copper at a temperature of 20 degrees celsius with resistivity no greater than [0.017241 (Ω.mm2/m); 0.15328(Ω.g/m)] comply with IEC 60028 (1925); Equivalent conductivity not less than 100% IACS.

- The quality insulating material is consistent with the insulation strength and temperature of CT.

- Insulation requirements between secondary windings: withstand voltage according to IEC 61869-2.

- Requirements for magnetic cores of current transformers

- The value of flexural dynamic force inflection point at rated frequency, when increased by 10% increases the excitation current by 50%.

- Residual magnetic coefficient for protective coils does not exceed 10%.

- Requirements for external insulation of current transformers

- Materials: Non-assembled cylindrical porcelain, canopy circle, brown color.

- Minimum creepage distance to meet the requirements of IEC 60815.

- Porcelain must have thermal, mechanical and electrical durability.

- Porcelain must be manufactured to meet the requirements of IEC 60137.

- Requirements for secondary terminal box of current transformers

- Material: Alloy or stainless steel, the thickness is not less than 1,5mm.

- Quantity of box: 01. For CT installed at metering points: secondary winding with accuracy level 0,2 and 0,5 for metering must be sealed for output of secondary winding.

- Cover box with gasket, hinge, lock handle. Terminal clamps is suitable for O-ring terminals for wires with a cross section of not less than 4 mm2.

- Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529.

- Cable ends entering boxes and cabinets must have cable termination connectors sized to match the diameter of the cable to ensure cable end robustness and tightness for boxes and cabinets (when there is no cable, these holes must be covered with a screw cap).

- Requirements for insulating oil

- The oil used in CT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

- The origin of oil, name, code and quantity of oil must be clearly stated in CT name plate.

- CT must be tight without leaking oil. Oil level indicator, oil sampling valve, oil drain valve, oil replenishment position.

- Mechanical requirements

- CT is capable of withstanding static loads according to table 7, standard IEC 61869-1, test time according to item 7.4.5, test diagram according to table 12, standard IEC 61869-1.

- Requirements for power arc

- The CT shall be able to withstand an internal arc in accordance with table 8, section 6.9, standard IEC 61869-1.

- Requirements for electromagnetic compatibility

- The level of radio frequency disturbance voltage generated within the CT shall comply with section 6.11, standard IEC 61869-1 (2007).

- The CT shall be capable of withstanding primary-to-secondary overvoltage with values ​​not exceeding the values ​​in table 9, standard IEC 61869-1 (2007).

### General Arrangement:

- Current transformers shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

- Unless otherwise stated, clearance from base of housing insullator to ground level must be at least 2250 mm.

### Requirements for accuracy class

- For secondary windings having accuracy class 0.2 and 0.5: Current deviation, phase displacement measured at secondary windings at rated power (25% - 100%), with errors not exceeding values ​​in table 11 , standard IEC 60044-1 (or table 201, standard IEC 61869-2).

- For secondary winding with accuracy of class 5P: Current deviation, phase displacement measured at secondary winding at rated power (25% - 100%), there is an error not exceeding value in table 14 , standard IEC 60044-1 (or table 205, standard IEC 61869-2).

### Requirements for specification sheet and label of current transformers

- Material made of stainless steel or oxidize. The handwriting is not faded during the life of current Transformers.

- The content on the parameter table can fully display the main current Transformers parameters according to IEC 60044-1, IEC 61869-2, IEC 61869-1.

### Requirements for testing

- The Type Test, Special Type Test, Routine Test for current Transformers shall comply with requiremens according to IEC 60044-1, IEC 61869-1, IEC 61869-2 and submition all test report enclosred tested current Transformers. There must be test report for oil and current Transformers accessory testing.

### Requirements for transporting of current transformers

- During transporting, it is do not not allow separate dismantling and packaging the components.

- Have solution to prevent moisture penetration and the impact of sea water.

### Requirements for documents of current transformers

- Manufacturer information, summary of current Transformers specifications, origin of current Transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, current Transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of current Transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Requirements for testing

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

- The Short-circuit withstand capability test must by one member of STL organization, have name in the list following: Intertek (ASTA, implemented before May 22, 2024)-UK; CESI-Italy; CPRI-India; ESEF ASEFA-France; JSTC-Japan; KEMA-Netherland; KERI-South Korea; PEHLA-Germany; SATS-Norway; STLNA-USA; VEIKI-Hungary; ZKU-Czech Republic.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

Type test report:

- The certificates required in according with IEC 60044-1, -2/IEC 61869-1, -2, including the following:

- Short-time current test;

- Temperature-rise test;

- Impulse voltage withstand test on primary terminals;

- Wet test for outdoor type transformers;

- Test for accuracy;

- Verification of the degree of protection by enclosures;

- Enclosure tightness at ambient temperature;

- Radio interference voltage measurement

Note: All tests have fully demonstrated the responsiveness of the equipment offered by bidder. The contractor may be rejected if does not meet the above requirements

- Routine Test

- Routine test is performed by the manufacturer on each product produced at the manufacturing facility. The routine tests are conducted in accordance with IEC 61869-1, -2 or TCVN 11845-2 or TCVN 7697-1 or equivalent standards, and include the following test items:

- Verification of markings

- Power - frequency withstand tests on primary terminals

- Power-frequency withstand test on secondary windings

- Power - frequency withstand test between sections

- Partial discharge measurement

- inter-turn overvoltage test

- Test for accuracy

- Check the housing for tightness at ambient temperature

- The test items must be fully tested according to the standards specified in the dossier of requirements or with standards equivalent to the specified standards.

- The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

### Requirements for accessories of current transformer

- The CT using insulating oil, a oil sampling device is required for periodic testing in operation; must have spare oil in service of repair.

- Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

### Requirements for transporting of current transformers:

- During transporting, it is do not not allow separate dismantling and packaging the components.

- There is a table listing the number of equipment and material supplies in each package.

- Have solution to prevent moisture penetration and the impact of sea water

### Requirements for documents of current transformers:

- Manufacturer information, summary of current Transformers specifications, origin of current Transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, current Transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of current Transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for current transformer

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

### Basic Data of 220kV Current Transformer

- Refer to Technical Data Sheet to have data of 220kV Current Transformer

## 35kV Current Transformers

### General

- Current Transformers of 35kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 105/QD-HDTV dated September 21, 2021 of EVN.

- Current Transformer (CT - Current Transformer) of the single-phase type, solid or liquid insulation (insulating oil), for outdoor installation, for electrical measurement in electrical systems with with isolated neutral or neutral earthed through impedance, rated voltage 35 kV

- For solid insulation CT, the insulating material must be made of epoxy resin (Epoxy resin), with good mechanical and electrical properties, able to withstand sudden temperature changes, and UV resistant. CT casting technology must be vacuum casting or pressure casting (APG) technology for epoxy insulation.

- For oil-insulating CT: The insulators must be glazed ceramics capable of working in heavily polluted conditions such as coastal areas, salt mist, industrial pollution, ultraviolet radiation, etc. as well as a humid tropical climate. The CT shell must be made from bearing steel, protected against rust and corrosion by electrostatic painting technology with a minimum coating thickness of 80µm. Insulating oil used for CT must be specifically used for transformers, without PCBs.

- Current transformers are designed, and tested in accordance with IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 or equivalent standards, meeting the specifications in the datasheet.

- Current transformers are designed using environmentally suitable insulating materials according to IEC 60815 - Guidelines for the selection of insulating materials with regard to contamination conditions.

- The primary terminals are made of tin-plated or nickel-plated copper to ensure the connection of copper conductors whose rated current corresponds to the primary current of the current transformer.

- The secondary terminals are located in the box located in body of CT. The secondary terminals are made of brass. Terminal box constructed of aluminum or aluminum alloy or stainless steel or hot-dip galvanized steel, resistant to changes in weather and with location for separate lead clamp sealing for measuring coils.

- Current transformers for protective functions shall fully satisfy the requirements for transient characteristics in accordance with the relevant standards.

- Current transformers are equipped with accessories, clamping terminals, together with bolts, nuts, washers suitable for aluminum wire, copper wire and wire cross-section according to the design.

### Installation arrangement

- The current transformer is designed to be suitable for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- Each current transformer must be equipped with earthing pole and allowed to connect to the main earthing grid for safety working purpose.

- Non-energetic metal structural parts of the current transformer must be grounded directly to the grounding system at the equipment installation location.

- The connection box must be able to withstand weather changes and have a protection level of IP55.

### Requirements for testing

Routine Test:

- The Routine Test for current Transformers shall comply with requirements according to IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 or equivalent, including the following test items:

+ Verification of makings.

+ Power-frequency voltage withstand test on primary terminals

+ Power-frequency voltage withstand test on secondary terminals

+ Power-frequency voltage withstand test between sections

+ Partial discharge measurement

+ Inter-turn overvoltage test

+ Tests for accuracy

Type Test:

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

- Type test must be performed and certified by an independent test laboratory certified to ISO/IEC 17025 on similar product samples. Type test is carried out according to IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 equivalent standards, including the following test items:

+ Short-time current test.

+ Temperature-rise test.

+ Impulse voltage withstand test on primary terminals.

+ Test for accuracy.

+ Wet test for outdoor type transformers.

+ Verification of the degree of protection by enclosures.

+ For solid insulation CTs, in addition to the above test items, the equipment shall be additionally tested item “Insulation aging test under UV radiation” according to ASTM D4587 or IEC 62217 or equivalent standards. Testing by an independent laboratory on a similar product sample.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements.

### Requirements for drawings and technical documents

The equipment shall be provided with the following drawings and technical documentation:

- Overview drawing of the size, mass

- Drawing depicting the structure.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

### Sample approval certificate:

The equipment must be certified by the Vietnam General Administration of Standards, Metrology and Quality (STAMEQ) for sample approval.

### Other requirement

Equipment is 100% brand new, no defects with full specifications certification of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements of the design and specified in the contract signed.

Equipment meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

Steel components (posts, beams, brackets, grounding, bolts, nuts, etc) must be hot-dip galvanized according to TCVN 5408:2007 and current equivalent standards on hot-dip galvanizing.

### Basic data for 35kV current transformer

Refer to Technical Data Sheet to have data of 35kV Current Transformer

## 500kV Capacitor Voltage Transformers

### General

Current voltage transformers of 500kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1816/QD-EVNNPT dated September 16, 2025 of EVNNPT.

The capacitor voltage transformer, put into operation for power transmission grid is the type single phase, sealed type, capacitor voltage transformer type, insulating oil, outdoor installation. Capacitor voltage transformer was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

Environment conditions:

- Climatic condition	: Tropical

- Average air temperature	: 25°C

- Maximum air temperature	: 45°C

- Minimum air temperature	: 0°C

- Average humidity	: 85%

- Maximum humidity	: 100%

- Seismic factor 	: 0.015g

- Creepage distance	: 25mm/kV

- Altitude above sea level	: <1000 m

Requirements of the electrical system installing the capacitor voltage transformer, TRV capacitor:

| Item | 500 kV system |
| --- | --- |
| Normal Voltage | 500 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 550 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |
| Grounding touching coefficient of transmission grid. | ≤ 1.4 |

500kV capacitor voltage transformer designed and manufactured meet working conditions comply with standards: IEC 61869-1 (2007), IEC 61869-3 (2011-07), IEC 61869-5 (2011-07), IEC 60071 (2011-03), IEC 60137 (2008-07), IEC 60871-1 (2014), IEC 60028 (1925), IEC 61850-7-3 (2010),  IEC 61850-7-4 (2010-03), IEC 61850-6.20 (2009), IEC 61850-6 (2009-12), IEC 61850-9-3 (2016-05), IEC 61869-9 (2016-4).

### Requirement temperature rise, insulation strength, vibration, short current circuit

The capacitor voltage transformer meet temperature rise requirement comply with standards: IEC 61869-5, IEC 60137.

The capacitor voltage transformer meet vibration requirement comply with standards: IEC 60068-1 (2013-10).

The capacitor voltage transformer meet insulation strength requirement comply with standards: IEC 60071-1, IEC 60060-1, IEC 60137, IEC 61869-5.

The capacitor voltage transformer is not damaged at rated voltage with thermal and mechanical impact of short circuit within 1s.

### Requirements for Partial discharge and pulse discharge

The capacitor voltage transformer has PD not exceed the limit follow table 3, IEC 61869-1.

The capacitor voltage transformer has ability to endure Multiple Chopped Multiple comply with 7.4.2, IEC 61869-1.

The capacitor voltage transformer has ability to endure Switching Pulse comply with table 2, IEC 60060-1.

The capacitor voltage transformer has secondary voltage when have overvoltage transferred from primary to secondary not exceed value at table 9, IEC 61869-1.

### Reliability requirements

Operation time until overhaul			: ≥ 10 years.

Total of operating time until to be replaced by a new CVT: ≥ 20 years.

### Requirements for component parts

          - Requirements for capacitor type divider

Each capacitor floor is an unconnected solid block with an insulated porcelain cover.

Each capacitor floor has an oil level indicator.

The Capacitor must to indicate insulation material

The capacitors must be comply with IEC 60871-1, IEC 60050-436.

          - Requirements for the electromagnetic unit

Case made of metal material does not corrode and rust.

Intermediate transformer: insulated copper coil. The coils are made of standard annealed copper at a temperature of 20 0C with resistivity no greater than [0.017241 (Ω.mm2/m); 0.15328(Ω.g/m)] comply with IEC 60028 (1925); Equivalent conductivity not less than 100% IACS.

There is inductance reactor coil with inductance according to section 3.1.537, standard IEC 61869-5.

There is damping device: overvoltage limit, prevent ferromagnetic resonance and temporary impacts.

There is a earthing switch.

There is discharge coils capable of continuous operation with current 1A, withstand short-circuit currents 50 A for 0.2s according to section 6.504.2 standard IEC 61869-5.

There is voltage limiting elements according to section 6.504.3 of IEC 61869-5 standard.

There is oil drain valve, oil sampling valve, earth switch, lightning protection, oil level indicator.

There is capacitance measurement positions C1, C2 and Cn.

The electromagnetic unit must be able to withstand lightning impulse voltages (peak values):

≥ Ulightning impulse voltages x C1/ (C1+C2)

The electromagnetic unit must be able to withstand short-term industrial frequency voltages (r.m.s.):

≥ UPrimary rated of CVT x 3.3x C1/ (C1+C2)

          - Requirements for secondary terminal box of capacitor voltage transformers

Material: Alloy or stainless steel. box with lid, located for sealing lead seals.

Quantity of box: 01.

Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529. Cable ends entering boxes and cabinets must have cable termination connectors sized to match the diameter of the cable to ensure cable end robustness and tightness for boxes and cabinets.

          - Requirements for external insulation of capacitor voltage transformers

Each capacitor voltage transformers divider, materials cylindrical ceramic porcelain, canopy circle, brown color.

Porcelain must have thermal, mechanical and electrical durability. Porcelain must be manufactured to meet the requirements of IEC 60137.

          - Requirements for insulating oil

The oil used in CVT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

The origin of oil, name, code and quantity of oil must be clearly stated in CVT name plate.

          - Requirement for CVT intermediate cabinets

Manufacturing materials: Inok 304 (stainless steel), thickness ≥ 3mm. Number of cabinets: 01 cabinets/3 CVT.

Cabinets must be made to meet tightness IP 55 according to IEC 60529. Cabinet door with lock, hinge, sink gasket. The bottom of the cabinet has cable holes to match the number and size of secondary cables. Terminal clamps is suitable for O-ring terminals for wires with a cross section of not less than 4 mm2.

In the cabinet, there must be sufficient accessories (circuit breaker, clamps, lighting leds, sockets ...) for: 3-phase combination of CVT, putting or separating each phase of CVT from operation.

          - Requirement for secondary cable

Secondary cable cabinet must be copper with multiple fibers, water resistant, oil resistant, fire resistant.

### Mechanical requirements, power arc

CVT is capable of withstanding static loads according to table 7, standard IEC 61869-1, time test according to item 7.4.5, test diagram according to table 12, standard IEC 61869-1.

The CVT shall be able to withstand an internal arc in accordance with table 8, section 6.9, standard IEC 61869-1.

### Requirements for electromagnetic compatibility (EMC)

Radio interference voltage (RIV) level generated within the voltage transformer shall comply with section 6.11, standard IEC 61869-1 (2007).

The voltage transformer shall be capable of withstanding primary-to-secondary overvoltage with values ​​not exceeding the values ​​in table 9, standard IEC 61869-1 (2007).

### Requirement for ferromagnetic resonance

The capacitor voltage transformer shall meet the value of ferromagnetic resonance according to Table 506, Section 6.502 and test according to Table 512, standard IEC 61869-5.

### Requirements for accuracy class of capacitor voltage transformers

For secondary windings having accuracy class 0.5: Voltage error and angle of phase difference must not exceed the value in Table 501, IEC 61869-5 standard.

For secondary winding with accuracy of class 3P: Voltage error and angle of phase difference must not exceed the value of Table 502, IEC 61869-5 standard.

### Requirements for grounding connection

The neutral grounding point of CVT must arranged in a position convenient for grounding with the system's earthing system.

The intermediate connection cabinets: The interior must have a common copper ground bar arranged with available holes and with enough bolts, nuts, washer.

### Requirements for specification sheet and label

Material made of Inok 304 (stainless steel). The handwriting is not faded during the life of capacitor voltage Transformers.

The content on the parameter table can fully display the main capacitor voltage transformers parameters according to section 6.13.501, standard IEC 61869-5.

### Requirements for testing, checking, installing, maintenance

The Type Test, Special Test, Routine Test for capacitor voltage transformers shall comply with requirements according to IEC IEC61869-1, -5 and submission all test report enclosed tested capacitor voltage Transformers.

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

The factory test record (Routine test) must be test intact voltage transformer without removing the components of the voltage transformer.

Routine test  must to be content accreditation error of measurement coils in variance errors and phase angle errors

Type test:

Type tests must be performed on a sample of a similar product. The certificates required in according with IEC 61869-1,3,5, including the following:

- Short – Circuit withstand capability test.

- Temperature - rise test;

- Capacitance and tan measurement at power-frequency.

- Impulse voltage withstand test on primary terminals;

- Chopped impulse test;

- Accuracy tests.

- Wet test for outdoor type transformer;

- Verification of the degree of protection by enclosures;

- Enclosures tightness test at ambient temperature;

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements.

- Routine tests:

Routine test is performed by the Manufacturer on each product manufactured at the Manufacturer. The following routine tests shall be carried out at the factory for each type of voltage transformer:

- Construction (general) inspection.

- Verification of markings.

- Power frequency withstand test on the primary terminals;

- Power frequency withstand test on secondary terminals;

- Power frequency withstand test between sections;

- Partial discharge test.

- Ferro-resonance check;

- Tests for accuracy.

- Enclosures tightness test at ambient temperature

The test items should be in full according to Table 10 of IEC 61869-5 Standard or equivalent.

The CVT manufacturer shall have a detailed technical procedure guiding the installation, maintenance, repair, overhaul and testing of CVT in operation (according to IEC 61869-1). There are instructions for oil sampling and adding oils.

### Requirements for transporting

During transporting, it is do not allow separate dismantling and packaging the components.

Have solution to prevent moisture penetration and the impact of sea water.

### Requirements for documents

Manufacturer information, summary of capacitor voltage transformers specifications, origin of capacitor voltage transformers accessories, quality management certificate.

There are all test records.

Generally drawings with dimensions, sectional drawings, structural drawings, capacitor voltage transformers structural details drawings and accessories drawings.

Instructions documents for installation, operation and maintenance of capacitor voltage transformers.

Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

There are instructions for oil sampling and adding oils. Assess the quality of oil.

The voltage transformer have accurary class 0,2 must to The certificate of approval of samples, the certificate of verification of measuring devices

### Requirements for testing

The type test, special test, routine test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

### Requirements for accessories

An oil sampling is required. Must have spare oil for CVT for repair (if the volume of CVT oil is large and the oil is not common)

Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

### Other requirements

If secondary coil of CVT manufacture by new technology, secondary circuit comply to IEC 61850-7-3 (2010); IEC 61850-7-4 (2010-03); IEC 61850-6.20 (2009); IEC 61850-6 (2009-12); IEC 61850-9-3 (2016-05); IEC 61869-9 (2016-04)

The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

### Basic Data of 500kV Capacitor Voltage Transformer

Refer to Technical Data Sheet to have data of 500kV Capacitor Voltage Transformer

## 220kV Capacitor Voltage Transformers

### General

- Capacitor Voltage Transformers of 220kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1816/QD-EVNNPT dated September 16, 2025 of EVNNPT.

- The capacitor voltage transformer, put into operation for power transmission grid is the type single phase, sealed type, capacitor voltage transformer type, insulating oil, outdoor installation. Capacitor voltage transformer was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition		: Tropical

- Maximum air temperature	: 45°C

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum humidity		: 100%

- Average humidity		: 85%

- Seismic factor 		: 0.15g

- Maximum wind velocity 		: 160 km/h

- Creepage distance		: 25mm/kV

- Requirements of the electrical system installing the capacitor voltage transformer:

| Item | 220 kV system |
| --- | --- |
| Normal Voltage | 220 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 242 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |

- Voltage transformer, designed and manufactured meet working conditions comply with standards: IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013)

### Requirement temperature rise, insulation strength, vibration, short current circuit

- The voltage transformer meet temperature rise requirement comply with standards: IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60137.

- The voltage transformer meet vibration requirement comply with standards: IEC 60068, IEC 60255.

- The voltage transformer meet insulation strength requirement comply with standards: IEC 60071-1, IEC 60060-1, IEC 60137, IEC 61869-5.

- The voltage transformer meet short current circuit requirement comply with standards: IEC 60044-2 and IEC 61869-5, IEC 60060-1.

### Reliability requirements

- Operation time until overhaul: ≥ 8 years.

- Total of operating time until to be replaced by a new CVT: ≥ 20 years.

### Requirements for component parts of capacitor voltage transformer

- Requirements for capacitor type divider

- Each capacitor floor is an unconnected solid block with an insulated porcelain cover.

- Each capacitor floor has an oil level indicator.

- Requirements for the electromagnetic unit

- Case made of metal material does not corrode and rust.

- Intermediate transformer: insulated copper coil.

- There is inductance reactor coil with inductance according to section 3.1.537, standard IEC 61869-5.

- There is damping device: overvoltage limit, prevent ferromagnetic resonance and temporary impacts.

- There is a earthing switch.

- There is discharge coils capable of continuous operation with current 1A, withstand short-circuit currents 50 A for 0.2s according to section 6.504.2 standard IEC 61869-5.

- There is voltage limiting elements according to section 6.504.3 of IEC 61869-5 standard.

- There is oil drain valve, oil sampling valve, earth switch, lightning protection, oil level indicator.

- There is capacitance measurement positions C1, C2.

- The electromagnetic unit must be able to withstand lightning impulse voltages (peak values):

≥ Ulightning impulse voltages x C1/ (C1+C2)

- The electromagnetic unit must be able to withstand short-term industrial frequency voltages (r.m.s.):

≥ UPrimary rated of CVT x 3.3x C1/ (C1+C2)

- Requirements for secondary terminal box of capacitor voltage transformers

- Material: Alloy or stainless steel. box with lid, located for sealing lead seals.

- Quantity of box: 01. For CVT installed at metering points: secondary winding with accuracy level 0.2 and 0.5 for metering must be sealed for output of secondary winding.

- Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529. Cable terminals come into cabinet must have suitable union with diameter and ensure the strengtheness for terminal and tighness of cabinet.

- Requirements for external insulation of capacitor voltage transformers

- Each capacitor voltage transformers divider, materials cylindrical ceramic porcelain, canopy circle, brown color.

- Porcelain must have thermal, mechanical and electrical durability. Porcelain must be manufactured to meet the requirements of IEC 60137.

- The capacitor must be compely with IEC 60050-151, IEC 60050-436.

- Requirements for insulating oil

- The oil used in CVT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

- The origin of oil, name, code and quantity of oil must be clearly stated in CVT name plate.

- Requirement for CVT intermediate cabinets

- Manufacturing materials: aluminum alloy or stainless steel. Number of cabinets: 01 cabinets/3 CVT.

- In the cabinet, there must be sufficient accessories (circuit breaker, clamps, lighting leds, sockets ...) for: 3-phase combination of CVT, putting or separating each phase of CVT from operation.

### Requirement for ferromagnetic resonance

- The voltage transformer shall meet the value of ferromagnetic resonance according to Table 7a, standard IEC 60044-5.

- The voltage transformer shall meet the value of ferromagnetic resonance according to Table 506, Section 6.502 and test according to Table 512, standard IEC 61869-5.

### Requirements for accuracy class of capacitor voltage transformers

- For secondary windings having accuracy class 0.5: Voltage error and angle of phase difference must not exceed the value in Table 11, IEC 61869-5 standard.

- For secondary winding with accuracy of class 3P: Voltage error and angle of phase difference must not exceed the value of Table 502, IEC 61869-5 standard.

### Requirements for grounding connection

- The neutral grounding point of CVT must arranged in a position convenient for grounding with the system's earthing system.

- The intermediate connection cabinets: The interior must have a common copper ground bar arranged with available drill holes and sufficient.

### Requirements for specification sheet and label

- Material made of stainless steel.

- The content on the parameter table can fully display the main capacitor voltage transformers parameters according to IEC 60044-2-5. The handwriting is not faded during the life of voltage Transformers. Capacitive voltage transformer according to section 6.13.501, IEC 61869-5.

### Requirements for testing, checking, installing, maintenance

- The Type Test, Special Type Test, Routine Test for capacitor voltage transformers shall comply with requiremens according to IEC 60044-2, -5 and submition all test report enclosred tested voltage Transformers. Capacitive voltage transformer according to Table 10, section 7, IEC61869-5.

- The CVT manufacturer shall have a detailed technical procedure guiding the installation, maintenance, repair, overhaul and testing of CVT in operation (according to IEC 61869-1). There are instructions for oil sampling and adding oils.

### Requirements for transporting of capacitor voltage transformers

- During transporting, it is do not not allow separate dismantling and packaging the components.

- Have solution to prevent moisture penetration and the impact of sea water.

### Requirements for documents of capacitor voltage transformers

- Manufacturer information, summary of voltage transformers specifications, origin of voltage transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, voltage transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of voltage transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- There are instructions for oil sampling and adding oils. Assess the quality of oil.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Requirements for testing Capacitor Voltage Transformers

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

- The Short-circuit withstand capability test must by one member of STL organization, have name in the list following: Intertek (ASTA, implemented before May 22, 2024)-UK; CESI-Italy; CPRI-India; ESEF ASEFA-France; JSTC-Japan; KEMA-Netherland; KERI-South Korea; PEHLA-Germany; SATS-Norway; STLNA-USA; VEIKI-Hungary; ZKU-Czech Republic.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

Type test:

- Type tests must be performed on a sample of a similar product. The certificates required in according with IEC 61869-1,3,5, including the following:

- Short – Circuit withstand capability test.

- Temperature - rise test;

- Capacitance and tan measurement at power-frequency.

- Impulse voltage withstand test on primary terminals;

- Chopped impulse test;

- Accuracy tests.

- Wet test for outdoor type transformer;

- Verification of the degree of protection by enclosures;

- Enclosures tightness test at ambient temperature;

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements.

- Routine tests:

- Routine test is performed by the Manufacturer on each product manufactured at the Manufacturer. The following routine tests shall be carried out at the factory for each type of voltage transformer:

- Construction (general) inspection.

- Verification of markings.

- Power frequency withstand test on the primary terminals;

- Power frequency withstand test on secondary terminals;

- Power frequency withstand test between sections;

- Partial discharge test.

- Ferro-resonance check;

- Tests for accuracy.

- Enclosures tightness test at ambient temperature;

- The test items must be fully tested according to the standards specified in the dossier of requirements or with standards equivalent to the specified standards.

- The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

### General Arrangement

- Voltage transformers shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

- Unless otherwise stated, clearance from HV terminal to ground is approximately 5300mm for 245kV capacitive voltage transformer. Clearance from base of housing insullator to ground level must be at least 2250 mm.

### Requirements for accessories of Capacitor voltage Transformers

- The CVT using insulating oil, a oil sampling device is required for periodic testing in operation; must have spare oil in service of repair.

- Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

### Basic Data of 220kV Capacitor Voltage Transformer

- Refer to Technical Data Sheet to have data of 220kV Capacitor Voltage Transformer.

Note: All 220kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 220kV CVT (WP 245 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021.

## 500kV TRV capacitor

### Type and Ratings

- Type:

- TRV capacitor shall be the single-phase, oil immersed, hermetically sealed outdoor post type 500kV voltage transformer, complying with IEC 60358.

- The TRV capacitor shall be fitted with necessary clamp and provided with necessary mounting bolts, nuts and washers.

- Ratings:

| Service condition | Outdoor |
| --- | --- |
| Type | Oil-impregnated paper |
| Rated voltage : | 500 kV |
| Highest system voltage: | 550 kV |
| Rated frequency | 50Hz |
| Rated insulation level |  |
| - Impulse withstand voltage : | 1550 kV (p) |
| Rated voltage factor and rated time: | 1.2 (continuous) 1.5 (30 seconds) |
| Temperature rise | 65oC |
| Rated capacitance | 15000 pF |
| Creepage distance : | min. 25 mm/kV |
| Isolator | Porcelain, brown |

### Design and Construction

- The protection of TRV capacitor shall be fully meet the requirements for transient performance in accordance with the relevant standards. A damping arrangement shall be made in order to effectively suppress the ferro-resonance oscillation.

### General Arrangement

- Bare stranded copper 120mm2 earthing wire and cosses and bolts, nuts and washers … shall be provided for connecting from equipment to supporting.

- The earthing terminals shall be provided for each piece of equipment in an approved function to enable the equipment to be bonded to the main earthing system.

### Tests and Inspection:

- Copies of the type test report with certificate issued by accredited testing laboratories which are accredited according to the international standard EN ISO/IEC 17025:2005. The certificate of Accreditation of the laboratory must be submitted as well.

### Type tests

Type tests shall be made in accordance with publication of IEC 60358-1 standard.

+ Discharge test;

+ Lightning impulse test;

+ Switching impulse test under wet conditions for the voltage range ≥300kV;

+ EMC radio interference voltage (RIV) tests;

- Routine tests

The following routine tests shall be carried out at the factory for each type of TRV capacitor in accordance with publication of IEC 60358-1 standard:

+ Tightness of equipment;

+ Capacitance and tan measurement at power-frequency;

+ Power frequency voltage withstand tests;

+ Measurement of partial discharge;

Note: All tests have fully demonstrated the responsiveness of the equipment offered by bidder. The contractor may be rejected if does not meet the above requirements.

### Basic Data of 500kV TRV Capacitor

- Refer to Technical Data Sheet to have data of 500kV TRV Capacitor.

## 35kV Voltage Transformers

### General

35kV voltage transformer according to Technical Standards for 22, 35 and 110 kV voltage transformers applied in Vietnam National Electricity Group, issued together with Decision No. 104/QD-EVN dated September 21, 2021. The standard number is: TCCS 07:2021/EVN

Voltage Transformer (VT) type 1 phase, solid insulation, or liquid insulation (insulating oil), outdoor operation. for electrical measurement in electrical systems with with isolated neutral or neutral earthed through impedance, rated voltage 35 kV

For solid insulation VT, the insulating material must be made of epoxy resin (Epoxy resin), with good mechanical and electrical properties, able to withstand sudden temperature changes, and UV resistant. VT casting technology must be vacuum casting or pressure casting (APG) technology for epoxy insulation.

For oil-insulating VT: The insulators must be glazed ceramics capable of working in heavily polluted conditions such as coastal areas, salt mist, industrial pollution, ultraviolet radiation, etc. as well as a humid tropical climate. The VT shell must be made from bearing steel, protected against rust and corrosion by electrostatic painting technology with a minimum coating thickness of 80µm. Insulating oil used for VT must be specifically used for transformers, without PCBs.

Voltage transformers are designed and tested in accordance with IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent standards, meeting the specifications in the datasheet.

Voltage transformers are designed using environmentally suitable insulating materials according to IEC 60815 - Guidelines for the selection of insulating materials with regard to contamination conditions.

The secondary terminals are in the box located in body of VT. The secondary terminals are made of brass. Terminal box constructed of aluminum or aluminum alloy or stainless steel or hot-dip galvanized steel, resistant to changes in weather and with location for separate lead clamp sealing for measuring coils.

Voltage transformers for protective functions shall fully satisfy the requirements for transient characteristics in accordance with the relevant standards.

Voltage transformers are equipped with accessories, clamping terminals, together with bolts, nuts, washers suitable for aluminum wire, copper wire and wire cross-section according to the design.

### Installation arrangement

The Voltage transformer is designed to be suitable for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

Each voltage transformer must have grounding terminals, allowing connection to the main grounding system for working and safety purposes.

Non-energetic metal structural parts of the equipment must be grounded directly to the grounding system at the installation location.

The connection box must be able to withstand weather changes and have a protection level of IP55.

### Requirements for testing

Routine Test:

The Routine Test for Voltage Transformers shall comply with requirements according to IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent, including the following test items:

- Verification of makings.

- Power-frequency voltage withstand test on primary terminals

- Power-frequency voltage withstand test on secondary terminals

- Power-frequency voltage withstand test between sections

- Partial discharge measurement

- Inter-turn overvoltage test

- Tests for accuracy

Type Test:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

Type test must be performed and certified by an independent test laboratory certified to ISO/IEC 17025 on similar product samples. Type test is carried out according to IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 equivalent standards, including the following test items:

- Short-time current test.

- Temperature-rise test.

- Impulse voltage withstand test on primary terminals.

- Test for accuracy.

- Wet test for outdoor type transformers.

- Verification of the degree of protection by enclosures.

- For solid insulation VTs, in addition to the above test items, the equipment shall be additionally tested item “Insulation aging test under UV radiation” according to ASTM D4587 or IEC 62217 or equivalent standards. Testing by an independent laboratory on a similar product sample.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements

### Requirements for drawings and technical documents

The equipment shall be provided with the following drawings and technical documentation:

- Overview drawing of the size, mass.

- Drawing depicting the structure.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

### Sample approval certificate:

The equipment must be certified by the Vietnam General Administration of Standards, Metrology and Quality (STAMEQ) for sample approval.

### Other requirement

Equipment is 100% brand new, no defects with full specifications certification of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements of the design and specified in the contract signed.

Equipment meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

Steel components (posts, beams, brackets, grounding, bolts, nuts, etc) must be hot-dip galvanized according to TCVN 5408:2007 and current equivalent standards on hot-dip galvanizing.

### Basic Data of 35kV Voltage Transformer

Refer to Technical Data Sheet to have data of 35kV Inductive Voltage Transformer.

## 500kV, 220kV Surge Arrester

### General

General conditions

Surge Arresters of 500kV, 220kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1158/QD-EVNNPT dated June 26 2025 of EVNNPT and Decision No. 2416/QĐ-EVNNPT date 09/12/2025 of the National Power Transmission Corporation promulgating regulations Regarding the adjustment and amendment of the basic technical specifications for 220 kV circuit breakers and the installation of 500 kV and 220 kV surge arresters in the transmission network.

The installation of surge arresters (CSV) at transmission substations must comply with Vietnamese regulations, national standards, and power industry standards, be tropicalized, and capable of stable and long-term operation under the environmental conditions of installation and operation at transmission substations, including natural climatic conditions.”

Environment conditions:

- Altitude above sea level	: <1000 m

- Climatic condition	: Tropical

- Maximum air temperature	: 45°C

- Minimum air temperature	: 0°C

- Average air temperature	: 25°C

- Maximum humidity	: 100%

- Average humidity	: 85%

- Maximum ground acceleration	: 0,22xg

- Averag wind speed	: 2m/s

- Creepage distance	: 25mm/kV

- Depending on the natural conditions of the equipment installation location, as determined in QCVN 02:2022/BXD, the above environmental condition values may be changed to suit the actual requirements to be applied.

Information for installation place

| Item | 500 kV system | 220 kV system |
| --- | --- | --- |
| Normal Voltage | 500 kV | 220 kV |
| Rated Frequency | 50 Hz | 50 Hz |
| Max operating voltage | 550 kV | 242 kV |
| Min operating voltage | 450 kV | 198 kV |
| Connection diagram | 3-phase 3-wire | 3-phase 3-wire |
| Neutral grounding mode | Direct | Direct |
| Ground fault factor of transmission grid | ≤1,4 | ≤1,4 |

Quality certificate requirements:

- The manufacturer must have a certificate of the quality management system (ISO 9001:2015 or equivalent, still valid) applied to the production of the surge arrester component parts. The manufacturer must have a factory testing laboratory with certified testing equipments.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, labels for commercial and technical, etc

### Requirements for component parts of surge arrester

Surge arrester

- Surge arresters (SA) for 500kV and 220kV substations shall be single-phase, gapless type, applied for phase-to-earth protection. For neutral protection or longitudinal overvoltage protection of equipment, separate operating conditions of the surge arrester must be calculated and parameters must be selected accordingly.

- Surge arresters (SA) for transmission substations shall be designed, manufactured, and tested for outdoor installation and continuous operation. The surge arresters must meet the requirements for insulation strength and temperature rise during long-term operation

- The structure and main components of the surge arrester (SA) include:

- SA housing and SA core;

- SA base insulator (depending on the case);

- Leakage current meter, Surge counter, accessories, and connecting conductors from the surge arrester to the common earthing system of the substation.

- The housing and core of the surge arrester (CSV) may be manufactured in multiple layers (multiple elements) firmly connected together to ensure mechanical strength throughout the processes of transportation, installation, operation, and maintenance of the surge arrester.

- The core of the surge arrester consists of non-linear resistors using metal oxide (MO) of ZnO type. MO has low resistance when overvoltage occurs and high resistance at the rated operating voltage of the power system.

- All parts of the surge arrester must be designed and manufactured so that, during operation under substation environmental conditions, no overheating occurs, and they must comply with the requirements on temperature rise of surge arrester components as specified in manufacturing standards.

- The surge arrester (CSV) must ensure mechanical strength, without cracks, fractures, or degradation; it must withstand the effects of the substation environment and electric field, the impacts that may occur in case of transmission line/substation faults, as well as the effects of atmospheric overvoltages and switching overvoltages.

- The surge arrester must be designed and manufactured so that, during installation, it does not violate the requirements for phase-to-earth and phase-to-phase clearances as specified in the Electrical Equipment Regulations and Safety Regulations for substations.

Surge Arrester Housing

- The surge arrester (CSV) housing shall be made of porcelain or polymer (silicone rubber) material, reinforced with load-bearing materials.

- For surge arresters with porcelain housings:

- The housing shall be structured as a sealed chamber and capable of releasing internal pressure through a pressure relief valve when the arrester operates under conditions exceeding its design capability.

- The pressure relief valve must ensure the tightness of the sealed arrester housing, preventing moisture ingress.

- For surge arresters with polymer housings:

- The polymer housing together with the arrester core shall be constructed to ensure the required mechanical strength (e.g., reinforced with fiberglass rods, load-bearing insulating rods, etc.), resistant to bending and torsion, and shall not deform or tilt under the load of connecting conductors.

- The housing material shall withstand natural environmental factors such as: water resistance, fungus resistance, dust resistance, acid resistance, crack resistance, resistance to solar radiation and ultraviolet (UV) rays, anti-aging properties, and capability of operating under conditions of salt fog, industrial pollution, coastal areas, and regions with high lightning density.

- The housing shall not discolor or develop stains, nor allow moss, fungus, or mold to appear during operation. The housing and external insulating sheds shall not be damaged by tearing or impact, and shall not crack or degrade due to environmental or electrical field stresses.

- The surge arrester housing must comply with insulation requirements for equipment at the corresponding voltage level as specified by withstand voltage values, creepage distance of the insulation, and the ability to withstand short-circuit currents that may occur at the substation. These values are specified in Table 2, Article 7, and may be adjusted depending on the installation location of the surge arrester within the power system.

- The surge arrester housing must be capable of withstanding static and dynamic forces that may act on the arrester, as calculated and determined by the consultant in the design documentation, or as additionally required in the procurement documents, in accordance with the arrester’s installation location.

- Equipotential ring requirements for the surge arrester:

- At the 500 kV voltage level, the equipotential ring is mandatory.

- At the 220 kV voltage level, it depends on the system and on the manufacturer’s technology.

- An additional equipotential ring may be installed at the top of the surge arrester to prevent corona discharge and to equalize the voltage distribution along the length of the arrester. The equipotential ring shall be made of metal or alloy capable of withstanding corrosion and rust caused by natural environmental conditions in substations, and shall have a structure suitable to create equipotential inside the sealed chamber of the surge arrester, thereby balancing the potential across the MO blocks.

Monitoring Components of the Surge Arrester (SA)

The surge arrester shall be equipped with the following monitoring components:

- Discharge counter indicating the number of operations (number of discharge events through the SA). The counter shall have a minimum of 5 digits.

- Leakage current meter indicating the operating condition (showing the leakage current through the SA). The leakage current meter may include a feature for transmitting signals to remote monitoring equipment. The meter’s display panel may indicate the SA operating status levels such as: normal operation threshold, warning threshold, and out-of-service threshold.

- The discharge counter and the leakage current meter may be provided separately or integrated into one device. The manufacturer’s instruction manual must clearly specify whether the leakage current meter indicates the total leakage current or only the resistive component of the SA.

- The requirements for connecting the Surge arrester operation monitoring components to the control room are only stated in the Design Document or Procurement Document in the case that the substation has been equipped with a remote Surge arrester operation data monitoring system (or will be equipped synchronously with the newly installed Surge arrester). The requirements for the connection procedure (protocol) and the information transmission line between the data reading monitoring system and the Surge arresters must be synchronized and ensure safety so that overvoltage does not spread from the Surge arrester to the substation control room.

Surge Arrester Base Insulation

- The surge arrester base insulation shall be made of porcelain or polymer, consistent with the arrester housing, for installation on the support structure. The base insulation shall withstand applied loads and ensure thermal, mechanical, and dielectric strength appropriate to the environmental conditions at the installation site.

Installation Arrangement

- The surge arresters shall be designed for direct installation on hot-dip galvanized steel supports. The steel used for the support structures shall have high strength and be capable of withstanding the loads of the surge arresters. The cross-sectional area of the support must be sufficiently large to meet the arrester manufacturer’s requirements, ensuring that during operation no excessive vibration of the arrester occurs which could affect its service life.

- Steel components (supports, beams, brackets, grounding parts, bolts, nuts, etc.) shall be hot-dip galvanized in accordance with TCVN 5408:2007, with a coating thickness not less than 80 µm, and shall comply with applicable standards for bolts and nuts.

- The grounding terminal of the surge arrester shall be marked with a “Earthing” symbol and positioned for convenient connection to the common grounding system of the substation. Grounding shall be carried out with insulated copper cable of cross-sectional area not less than 90 mm², with clamps suitable for proper connection.

- The leakage current meter and the discharge counter shall be installed in positions convenient for operation and maintenance, while considering and avoiding environmental impacts of the substation.

- Each surge arrester shall be provided with a nameplate and rating plate made of aluminum alloy, copper alloy, or stainless steel (Inox 304), showing all the main parameters of the arrester in accordance with manufacturing standards. The data on the rating plate and nameplate shall be durable, resistant to fading, and remain legible throughout the service life.

- High-voltage terminals and connecting leads of the surge arrester shall be selected and calculated in accordance with the arrester’s voltage rating, nominal discharge current, and terminal load capacity, ensuring safe and reliable operation.

- During installation, the manufacturer’s installation procedures for the surge arrester shall be strictly followed. Only accessories and materials of assured quality and approved by the manufacturer shall be used. The entire installation process must strictly comply with the manufacturer’s prescribed installation sequence.

Accessories

- The surge arrester shall be supplied complete with all necessary accessories for connection to phase/neutral conductors and the grounding system, as well as insulating mounting accessories for installation on metal support structures, and a lightning counter, including but not limited to:

- Suitable terminal clamps for connection to phase/neutral conductors and the grounding system.

- Grounding clamps and bolts compatible with copper conductors.

- Bolts, nuts, washers, and anti-loosening devices made of stainless steel or hot-dip galvanized steel.

- Surge arrester support structures and brackets (if any).

- Surge arrester mounting base.

- Accessories for connecting the lightning counter, insulating accessories for installation on metal support structures.

- Isolating switch (applicable in certain special cases in substations).

Other Requirements

- The equipment supplied shall be brand new, 100% unused, free from defects, accompanied by clear and legitimate Certificates of Origin (CO) and Certificates of Quality (CQ), together with supporting documents demonstrating compliance of the supplied goods with the design requirements and contractual provisions.

- The Bidding Documents or Equipment Procurement Contract shall include provisions requiring the Manufacturer to commit to warranty obligations in accordance with current commercial regulations as well as the requirements regarding the technical service life of the equipment.

Basic Technical Parameters of Surge Arresters

- The table of basic technical parameters of surge arresters: detailed in Technical Data Sheet

Requirements on Equipment Lifetime

The reliability and lifetime requirements of the surge arrester (SA) shall be determined under the following minimum conditions:

- Number of discharge operations at rated discharge current without damage to the SA: at least 10 times.

- Service lifetime of the SA: at least 20 years.

Requirements on Surge Arrester Testing

- General requirements on surge arrester test documents:

- The manufacturer or supplier of surge arresters shall be responsible for providing complete test reports of surge arresters as specified in the Standards applied for surge arrester manufacturing.

- The technical specification shall stipulate the minimum tests that the manufacturer or supplier must provide prior to participating in equipment procurement bidding and prior to delivery to the purchaser.

- Requirements on surge arrester testing:

The minimum testing requirements for Surge arrester are stated in under requirement of this Regulation and will be adjusted by EVNNPT with additional documents based on the contents specified in the Surge arrester manufacturing Standards:

Test requirement for Surge arrester:

i. For Surge arrester apply the following standards: IEC60099-4, IEEE C62.11, GB/T 11032, …:

- Type test:

The manufacturer must provide documents proving that it meets the minimum type tests according to IEC 60099-4 as follows:

- Insulation withstand test on the arrester housing.

- Residual voltage test.

- Long-term operating condition test with Ucov (Test to verify long-term stability under continuous operating voltage).

- Repetitive charge transfer withstand (Qrs).

- Heat dissipation behavior verification of test sample.

- Operating duty test.

- Power frequency voltage versus time.

- Short circuit test.

- Bending test.

For Surge arrester s using polymer insulation, the following additional tests are required:

- Weather aging test.

Type test reports must be performed by an ISO/IEC 17025 accredited laboratory or the manufacturer's laboratory, but the test results must be witnessed by independent testing agencies with ISO/IEC 17025 certification such as: KEMA, CESI, ASTA, members of the STL association, etc.

- Routine test:

The Surge arrester manufacturer must provide at least the routine test reports (factory tests) for the following types of tests according to IEC 60099-4:

- Reference Voltage measurement (Uref).

- Residual Voltage Test (Ures).

- Internal Partial Discharge Test.

- Power Frequency Voltage Test.

The Surge arrester routine test reports are performed by the Surge arrester manufacturer himself and the test results are issued.

ii. For Surge arrester apply the following standards ГОСТ Р 52725:

- Compliance tests (Kвалификационные):

The manufacturer must provide documents proving compliance with at least the compliance tests (Kвалификационные) according to the GОСT Р 52725 standard as follows:

- Reference voltage test (Классификационное напряжение).

- Residual voltage test (Остающееся напряжение при токе).

- Possibility of repeated transduction (Пропускная способность).

- The ability to absorb heat (Тепловая устойчивость).

- CSV shell insulation test (Электрическая прочность изоляции).

- Operational endurance test (Характеристика «напряжение- время»).

- Mechanical Tests (Механическая прочность и Стойкость к вибрации).

The compliance test reports (Kвалификационные) must be performed by an ISO/IEC 17025 accredited Laboratory or by the manufacturer's Laboratory, but the test results must be witnessed by an independent testing body with ISO/IEC 17025 certification.

- Acceptance testing (приемо-сдаточные):

The Surge arrester manufacturer must provide at least acceptance test reports (factory tests) for the following types of tests according to the standard ГОСT Р 52725:

- Reference voltage measurement (Классификационное напряжение).

- Residual voltage test (Остающееся напряжение при токе).

- Partial discharge test (Уровень частичных разрядов).

Acceptance test protocols (приемо-сдаточные) of Surge arrester are carried out by the Surge arrester manufacturer himself and the test results are issued.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements

Requirements on Surge Arrester Transportation

- Surge arresters shall be designed to allow easy disassembly, with each part packaged separately together with a packing list of materials for each package. They must be convenient for storage, transport (by machine or manual handling), and must allow for easy reinstallation and operation.

- Each surge arrester package shall be accompanied by a packing list of all items included. Measures shall be taken to prevent ingress of moisture, as well as the effects of seawater, thunderstorms, and other environmental factors.

Requirements for documents of Surge arrester

- The manufacturer shall be responsible for providing the following documents in full:

- Table of required surge arrester parameters.

- Drawings describing the structure, dimensions, and cross-sections of the main components of the surge arrester.

- Installation drawings (including drawings of equipment supports).

- Test reports in compliance with this Regulation and the applicable standards.

- Certificates of quality management system, product origin, and accessories.

- Manuals and recommendations covering: packaging, transportation, installation, operation, inspection, repair, equipment and accessory maintenance, periodic testing, type tests (including frequency and scope of work); common defects and failures; and troubleshooting methods.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

Other Requirements for Surge Arresters

- Other requirement according to Decision No. 1158/QD-EVNNPT dated 27/06/2025: Regulations on basic technical characteristics of 500 kV and 220 kV lightning arresters in transmission grid transformer stations.

- Items not specified in the “Basic Technical Specification of 500 kV and 220 kV Surge Arresters in Transmission Substations” shall comply with EVN and EVNNPT technical regulations, TCVN standards, and equivalent international standards.

Basic Data of 500kV, 220kV Surge Arrester

Refer to Technical Data Sheet to have data of 500kV, 220kV Surge Arrester

## 110kV, 35kV Surge Arrester

110kV, 35kV Surge Arresters according to the basic technical specification of transmission grid equipment, issued under Decision No. 110/QD-HDTV dated September 21, 2021 of EVN.

### General requirements:

- To ensure lightning protection, valves used for substations and distribution substations/switches that can protect both overvoltages due to lightning waves and overvoltages of operation, it is required to use a type of surge arrester. gapless lightning valve.

- SA has a shell made of porcelain (Porcelain) or Polymer, inside there are nonlinear MO resistors using ZnO type. MO has a small resistance value at overvoltage and a large value at rated operating voltage of the power system. If the shell is made of Polymer, the core must have a structure that ensures mechanical strength (such as fiberglass rods, load-bearing insulation bars, etc.) or impact, not cracked, cracked, degraded by environment and electric field.

- There is a self-relieve pressure in overload operating conditions for porcelain-shell valve SA.

### General Arrangement:

- SA must be designed for direct mounting on steel supports.

- SA must be fully equipped with accessories for connection to the line/neutral line and grounding system, insulation kit for mounting on metal rack systems and lightning counters.

### Test requirements:

- SA must be testing comply with the latest edition of IEC 60099-4 or equivalent.

Routine test:

- The Routine test shall comply with the latest edition of IEC 60099-4 and as follows:

- Reference Voltage;

- Residual Voltage.

- Inter partial discharge test.

- Power - frequence voltage test

Type test:

- SA must be performed by an ISO laboratory or manufacturer's laboratory but test results must be witnessed by independent international testing bodies (with ISO certifications), such as: KEMA, CESI etc.

- Type test comply with the latest edition of IEC 60099-4 or equivalent and as follows:

- Insulation withstand test on the arrester housing.

- Residual Voltage;

- Test to verify long term stability under continous operation voltage)

- Repetive charge transfer withstand

- Heat dissipation behaviour verification of test sample.

- Operation duty test.

- Power Frequency voltage versus time -TOV.

- Short circuit test.

- Bending test.

- For Polymer-housed surge arresters: Weather ageing test.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements

### Accessories

- Terminal clamps for connections.

- Bolt-type grounding clamps compatible with copper conductors.

- Corresponding bolts and nuts.

- Surge arrester support structures and brackets (if any).

- Surge arrester mounting base.. Lightning counter.

- Disconnector (applicable for surge arresters in substations/switchgear).

### Drawings and Technical document:

- Equipment shall be provided with the following drawings and technical documentation:

- Drawing depicting the structure.

- Installation instructions drawings (including equipment bracket drawings).

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements:

- Equipment is 100% new and original, without defects, has a clear and legal certificate of origin (CO) and has a certificate of goods quality (CQ), together with relevant documents to prove it. Verify that the goods provided are in accordance with the design requirements and specified in the signed contract.

- Surge arresters must meet the durability requirements for climate and environmental conditions in Vietnam: tropicalized, suitable for operating environment conditions.

- Steel structure, beams, brackets, grounding, bolts, nuts and steel parts are hot-dip galvanized with coating thickness in compliance with Decision No. 82/QD-EVN-QLXD-TD dated 07/01/2003.

- Bolts manufactured according to TCVN 5571-1991, TCVN 1916-1995; nuts - washers according to standard TCVN 1905-76.

- It is permissible to unpack and pack each part separately for transport and a list of the number of supplies in each packing is required.

### Basic Data of 110kV, 35kV Surge Arrester:

Refer to Technical Data Sheet to have data of 110kV, 35kV Surge Arrester

## Neutral reactor

### General requirements

The design of the reactors shall be based on the following conditions and requirements:

- The reactors shall be designed for outdoor installation at the prevailing site conditions without any restriction.

- The maximum permissible winding average temperature rise shall not exceed 90K at highest operation voltage, etc. at specified rated continuous current for neutral grounding reactors.

- Neutral-grounding reactors shall be capable of withstanding the specified rated short time current for at least 10 seconds.

- The reactors shall be naturally air-cooled (AN).

- Neutral grounding reactors shall also be designed under consideration of the basic requirements as per ANSI/IEEE Std. 32, IEC 60076-6

- Furthermore, each reactor shall comply with the stipulations of the following Articles.

### Basic Data

| Type | : | Outdoor, dry type, single phase |
| --- | --- | --- |
| Rated voltage | : | 123kV |
| Rated impedance (at 250C) | : | 1100/1300/1500 Ω |
| Rated current | : | 15A |
| Rated short circuit current within 5s | : | 145 Apeak – 105Arms |
| Rated short circuit current within 0.2s | : | 170 Apeak – 120 Arms |
| Temperature rise of winding | : | 600K |
| Cooling method | : | AN |
| Insulation classs | : | F |
| Rated insulation level: |  |  |
| - Lightning impulse withstand voltage | : | 550 kV |
| - Power frequency withstand voltage | : | 230 kV |

### Windings

- All reactor windings shall have uniform insulation, and the windings of neutral-grounding reactors shall be insulated commensurate with the neutral terminals to which the reactors shall be connected.

- Particular values for insulation and test levels shall be obtained from the description of the Technical Data Sheets of these Bidding Documents.

- Aluminium of a high conductivity and insulation material of high quality shall be used. The thermal class of insulation shall comply with class F as per IEC 60085 and IEC 60726. The insulation material of windings and connections shall be of resin impregnated fiber-glass encapsulation, free from insulation compositions subject to shrinking or collapse during service, and none of the material shall disintegrate or become brittle under all load conditions.

- The coils and spider arms etc. shall be completely painted with a high-quality two-pack polyurethane-based insulation paint hardened with aliphatic iso-cyanate resin and shall be of colour code RAL 7032 (silica-grey). The dry-film thickness shall be min. 40µm.

- The coils must be capable of withstanding movement and distortion caused by all operating conditions. All leads or bars from the windings shall be rigidly supported. Stresses on coils and connections must be avoided.

- The Contractor shall demonstrate the ability of withstanding thermal short circuits for the windings after full load by a calculation in accordance with IEC 60076-5. For this purpose, the temperature value shall be assumed with 1400C for class F to be the initial temperature before short circuit. The max. permissible value of the average temperature of the windings after short circuit shall not exceed 2000C for aluminium windings.

### Magnetic Core

- An air-core (core-less) type of core shall be provided.

- A computer analysis/diagram shall be submitted (along with the Technical Data Sheets to be submitted for approval), showing the effects of the magnetic field and advising the minimum magnetic clearances to any other metallic parts to be considered for installation.

### Terminals, Insulators and Structure

- Suitable terminals shall be provided on spider arms on top and bottom of the reactors. All necessary bi-metallic and other parts required for proper connection of all conductors to be connected shall be included in the supplies.

- Post insulators shall be of the outdoor type designed for areas with a medium polluted atmosphere (pollution level heavy 3). They shall correspond to IEC 60815, shall be free from defects and shall be thoroughly vitrified. In case of spacer insulators between phases their creepage distance shall be increased accordingly.

- Insulators shall be of top-quality electrical grade porcelain, homogenous and non-porous, and shall be in one piece. The glaze shall not be depended upon for insulation and shall be of a uniform shade of brown, completely covering all exposed parts of the insulator.

- If required, extension brackets of anti-magnetic material shall be supplied by the reactor manufacturer to maintain the magnetic clearances. Mounting rings and/or other suitable stiffening facilities shall be also supplied to facilitate the mounting of the post insulators to the mounting pad.

- The installation level above ground shall be 2.5m unless a fencing is provided under full consideration of the magnetic clearances to be advised by the reactor manufacturer. Suitable additional structure shall be provided by the Contractor to fulfil these requirements.

- Appropriate earthing terminals of adequate size as required for safe operation shall be provided and installed at extension brackets, structure and mounting rings etc.

### Inspections and Tests

- Each of the reactors shall be subjected to inspections and witness tests to be performed at the manufacturer’s premises and test shop, recognised and certified at least by ISO 9001, and at site, as specified hereinafter to verify their conformity with the guaranteed and other design data. The Contractor is obliged to submit a detailed test program for approval in due time, prior to the tests (at the latest three months before testing). Detailed test schedules separately for each unit showing day-wise when each of the witness tests will be carried out (max. 10 hours per working day) shall be submitted for approval along with the test program as above.

- All tests other than impulse tests shall be performed with the original insulators and extension brackets etc. installed. Performance of any tests on the reactors other than impulse tests, while hanging on a crane, will not be accepted.

- The tests shall be performed in accordance with the latest issues of the Recommendations of the International Eletcrotechnical Commission (IEC-standards), and ANSI/IEEE Std. 32 (as general guide only), supplemented by these specifications.

- The following tests shall be performed in the presence of the Purchaser or his Representative:

### Requirements on testing and laboratory

- The general requirements for routine, type and special tests shall be as prescribed in IEC 60076-6 Standard;

- The Bidder is required to submit type test, routine test, special test to demonstrate the responsiveness of the equipment offered by bidder;

- The type test reports are performed and issued by the following laboratories:

+ Internationally recognized testing laboratories which are members of STL (Short-Circuit Testing Liaison) organization; or

+ The type test reports are performed by the internationally recognized testing laboratories which are accredited according to the international standard EN ISO/IEC 17025:2017, with witnessed and issued by internationally recognized testing laboratories which are members of STL; or

+ Internationally recognized testing laboratories accredited according to the international standard EN ISO/IEC 17025:2017 which are members of ILAC (International Laboratory Accreditation Cooperation) or laboratories located at G7 or EU which perform and issue the above-mentioned standards.

- Routine tests:

- Measurement of winding resistance. - Measurement of the impedance at continuous current. - Measurement of loss at ambient temperature. - Winding overvoltage test for neutral-earthing reactors.

- Type tests:

- Short-circuit test for neutral-earthing reactors to be connected to a neutral of a power system and for test reactors; - Temperature rise test at rated continuous current; - Lightning impulse test for current-limiting reactors; - Switching impulse test.

- Special Tests:

- Short-circuit test for current-limiting reactors, neutral-earthing reactors to be connected to a neutral of a power system and for test reactors;

- Measurement of reactance of the winding in the case of gapped-core and magnetically shielded air-core reactors;

- Measurement of acoustic sound level;

- Separate source a.c. withstand voltage test for dry-type reactors mounted on support insulators;

- Measurement of loss close to reference temperature in case of liquid-immersed reactors

- Measurement of vibration at rated continuous current for liquid-immersed reactors;

- Switching impulse test;

- Double-ended lightning impulse test;

- Measurement of coupling factor;

- Wet winding overvoltage test;

- Wet separate source a.c. withstand voltage test for dry-type reactors mounted on support insulators.

All tests have fully demonstrated the responsiveness of the equipment offered by the bidder. The contractor may be rejected if it does not meet the above requirements

## Neutral resistor

### Basic Data

| Type | : | outdoor, single phase |
| --- | --- | --- |
| Rated voltage | : | 52 kV |
| Rated current | : | 15A |
| Rated frequency | : | 50Hz |
| Rated resistance | : | 60 |
| Rated energy absorption | : | 7 MJ |
| Rated short circuit current within 5s | : | 145 Apeak – 105Arms |
| Rated short circuit current within 0.2s | : | 170 Apeak – 120 Arms |

### Requirements on testing and laboratory

- Routine Tests

- Compliance with IEC/ANSI/ IEEE standard.

- Type Tests

- Type test reports submitted for neutral resistor similar to the supplied product tested at or issued by independent testing laboratories .

- Site Tests (minimum requirements)

- Compliance with IEC/ANSI/ IEEE standard.

- Other tests as per the EVN/EVNNPT regulations

## Post Insulator

### General

Post insulator according to the basic technical specification of transmission grid equipment, issued under Decision No. 103/QD-HĐTV dated July 11, 2019 of EVNNPT

Post insulator put into operation for power transmission grid is the type using single phase and outdoor. Post insulator was designed and manufactured by material such as porcelain and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition		: Tropical

- Maximum air temperature	: 45°C

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum humidity		: 100%

- Average humidity		: 85%

- Seismic factor 		: 0.15g

- Maximum wind velocity 		: 160 km/h

- Creepage distance		: 25mm/kV

- Requirements of the electrical system installing the post insulator

- ????????????

| Item | 500 kV system | 220 kV system |
| --- | --- | --- |
| Normal Voltage | 500 kV | 220 kV |
| Rated Frequency | 50 Hz | 50 Hz |
| Max operating voltage | 550 kV | 242 kV |
| Grounding touching coefficient of transmission grid | ≤ 1.4 | < 1.4 |

- The support insulators required herein shall conform to the requirements of IEC 60071-1:2011, IEC 60071-2:2018, IEC 60168:2001, IEC 60273:1990, IEC 60437:1997, IEC 60507:2013, IEC 60660:1999, IEC 60815-1:2008, IEC 60815-3:2008, IEC 60815-3:2008.

### Basic physical characteristic of post insulator

- Voltage technical characteristic:

- Lightning impulse withstand voltage in dry condition.

- Power frequency withstand voltage in wet condition.

- Post insulator Puncture voltage.

- When we caculate the basic voltage for post insulator which will install on the future, and insulation co-ordinate with other equipments in substation we should use some standard below:

- IEC 60071 In the normal condition of working.

- IEC 60815 In the polution condition of working.

- Mechanical technical characteristic:

- Regulations about minimum failing load.

- Regulations about the dimension of post insulator, minimum nominal creepape distance

- Deflection when faced the bending strength

- Environment and other characteristic:

- Interference and anti-Interference of  Radio wave.

- Artificial polution

### Basic data for Post insulator

              - 500kV post insulator

| Nominal system voltage | 500kV |
| --- | --- |
| Rated voltage | 550kV |
| Switching impulse withstand voltage, peak | 1175 kV |
| Lighting impulse withstand voltage 1.2/50µs | 1550 kV |
| Minimum failing load |  |
| Bending | 10,000 N |
| Torsion | 4,000 Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

              - 220kV post insulator

| Nominal system voltage | 220kV |
| --- | --- |
| Rated voltage | 245kV |
| Lightning Impulse withstand voltage (1.2x50us) | 1050 kV |
| Power frequency withstand voltage, wet | 460 kV |
| Minimum failing load |  |
| Bending | 10,000 N |
| Torsion | 4,000 Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

              - 110kV post insulator

| Nominal system voltage | 110kV |
| --- | --- |
| Rated voltage | 123kV |
| Lightning Impulse withstand voltage (1.2x50us) | 550 kV |
| Power frequency withstand voltage, wet | 230 kV |
| Minimum failing load |  |
| Bending | 10,000 N |
| Torsion | 4,000 Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

              - 35kV Post Insulator

| Nominal system voltage | 35 kV |
| --- | --- |
| Rated voltage | 38,5kV |
| Lightning Impulse withstand voltage (1.2x50us) | 185kV |
| Power frequency withstand voltage, wet | 80 kV |
| Minimum failing load |  |
| Bending | 10,000 N |
| Torsion | 2,500 Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

### Minimum creepage distance:

- Minimum creepage distance should caculate base on Vietnamese standards and belong to environment condition where we put the post insulator. In this project the Minimum creepage distance is 25mm/kV.

### Mechanical characteristic

Regulation about Falling load of Post insulator on the test for bending

|  | Post insulator designation | Falling load (N) |  |  |
| --- | --- | --- | --- | --- |
|  |  | Load-bending | Moment-torsion |
| 500kV (C10-1550) | Class 10 | 10000 | 4000 |
| 220kV (C10-1050) | Class 10 | 10000 | 4000 |
| 110kV (C10-550) | Class 10 | 10000 | 4000 |
| 35kV (C10-200) | Class 10 | 10000 | 2500 |

Regulation about dimension of Post insulator

- Porcelain post insulator with metal inside  should follow section 3 – Table 1 of IEC 60273.

Regulation about surface of Post insulator

- With post insulator use porcelain, we should use the post insulator which have equal enamel layer, equal colour, no cracked, no spot. The surface of post insulator should identical along the post insulator.

### Requirements for testing

- Test for post insulator shall comply with requiremens according to IEC 60168 2001 and should test report include post insulator.

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025.

- Post insulator maintenance must follow the requirement, recommendation of manufacture as well as the regulations of operation unit.

Type Tests

- Type tests shall be made on all post insulators in accordance with the latest publication of IEC 60168.

- Dry lightning impulse withstand voltage test;

- Wet switching impulse withstand voltage test (applicable to post insulators for use on system with highest voltage for equipment above 50kV);

- Wet power frequency withstand voltage test;

- Mechanical failing load test.

Special test:

- Test for deflection under load;

- Radio interference test (IEC 60437);

- Artificial pollution test (IEC 60507).

Sample Test

- Sample tests shall be made on all post insulators in accordance with the latest publication of IEC 60168.

- Applicable on the number of post insulators selected at random from the lot:

- Verification of the dimensions;

- Temperature cycle test;

- Mechanical failing load test;

- Porosity test for ceramic insulators;

- Galvanizing test.

Routine Test

- Routine test shall be made on all post insulators in accordance with IEC 60168. Every post insulator shall be subjected to the applicable tests carried out in the following order:

- Routine visual inspection;

- Routine mechanical test (bending test), height >770mm..

All tests have to fully demonstrate the responsiveness of the equipment offer by bidder. The contractor may be rejected if does not meet the above requirement

Requirements for transporting of post insulator

- Post insulator have to easily for removing, packing, transport by machine or handiwork and have easily allow for installing, operation.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration and the impact of sea water.

Requirements for documents of post insulator

- Manufacturer information, summary of post insulator specifications, origin of post insulator accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, post insulator structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of post insulator.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

Other requirements for post insulator

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

500kV, 220kV, 110kV, 35kV Post Insulator

Refer to Technical Data Sheet to have data of 500kV, 220kV, 110kV, 35kV Post Insulator.

## STRING INSULATOR

### General requirements:

- Technical standards for glass and ceramic insulators on EVNPT's transmission grid according to Decision No. 1769/QĐ-HĐTV dated 9/9/2025.

- String insulator put into operation for power transmission grid is the type using ceramic, glass. String insulator designed, made with material and technology which are checked, tested, supplied, transportation shall comply with TCVN, EVN and IEC.

- Insulator has snap cap shape, out-door and proper with tropical and temperate zone, fog, heavy duty, and lightning zone.

### Codes and standards

It is the intent of this specification to allow the supply of insulators according to IEC standard or other equivalent standards. The standards which shall be used in this Specification are listed below. Any standard proposed by the Bidder in place of or in addition to those specified shall be added.

- BS 137 Insulators of ceramic material or Toughened Glass for overhead lines with nominal greater than 1000V.

- IEC 60305 (1995-12) Insulators for overhead lines with a nominal voltage above 1000 V - Toughened Glass or ceramic insulator units for a.c. systems - Characteristics of insulator units of the cap and pin type.

- IEC 60383-1 Insulators for overhead lines with a nominal voltage above 1000 V - Part 1: Toughened Glass or ceramic insulator units for a.c. systems - Definitions, test methods and acceptance criteria

- IEC 60383-2  Insulator strings and insulator sets for A.C. systems - Definitions, test methods and acceptance criteria.

- IEC 60120 (1984-01) Dimensions of ball and socket couplings of string insulator units.

- IEC/TR 60575 (1977-01) Thermal-mechanical performance test and mechanical performance test on string insulator units.

- IEC/TR 60797 (1984-01) 	Residual strength of string insulator units of Toughened Glass or ceramic material for overhead lines after mechanical damage of the dielectric

- IEC/TR 61211 Ed.2 (2004-11) Insulators of ceramic material or Toughened Glass for overhead lines with a nominal voltage greater than 1000V-Puncture testing

- IEC 60815  Guide for the selection of insulators in respect of polluted conditions.

- IEC/TR 61467 (Ed.1.0 2008-08) Insulators for overhead lines with a nominal voltage above 1000V-A.C power arc tests on insulator sets.

- IEC 60437 Ed.2 (1997-09) 	Radio interference tests on high voltage insulators.

- IEC 60060-1: High voltage test techniques – Part 1: General definitions and test requirements.

- IEC 60507: 1991-04: Artificial pollution test on high voltage insulators to be used on A.C. systems.

- IEC 60372: 1984-1 and Amendment No.1: 1991-09: Locking devices for ball and socket couplings of string insulator units – Dimensions and tests.

- IEC 60071-1 Ed.8: 2011-03: Insulation co-ordination – Part 1: Definitions, principles and rules.

- IEC 60071-2 Ed.8: 1996-12: Insulation co-ordination – Part 2: Application guide.

- Decision No. 1769/QĐ-HĐTV dated 09/09/2025: Regulations on basic technical characteristics of glass and ceramic insulators on transmission grids

### Requirements about structure and technical characteristic

- Insulator is string ball and socket type according to IEC 60305 and 60120, the upper part of insulator is cylinder, out door type, and proper with tropical and temperate zone, fog, heavy duty, and lightning zone.

- Cap and pin will not oxygenate, getting out of shape when they faced the mechanical load, making the change of distance of each insulator or rising the pressure on insulator.

- Cap make by cast iron or allumimum alloy and steel galvanized. Cap should round, in and outside part should concentric, no breaking, no roll up, no pock-marked, outside boundary will not rough to reducing electromagnetic concentration and making the interference of radio wave.

- Insulator make by glass or ceramic. The head of insulator where It will connect to pin should cylinder shape, this make the equal of pressure in insulator. Glass insulator have no fault as impurities, spume and the surface of insulator should identical.

- Pin make by forged steel and galvanized steel. Zinc sleeve on pin should follow IEC 61325 standard.

- The cement used to connect between cap and insulator as well as insulator and pin must be Aluminous, Portland cement that meets the requirements for inspection and testing of suspension insulators according to IEC 60305, IEC 60383, IEC and equivalent standards

- To avoid the slot between cap and glass insulator for reducing photo-electric, this slot must connect (can be insert by synthetic) and connect with electric paint, with the purpose when operation will not cause pock-marked  in this boundary and lead to photo-electric and interference.

- Cotter pin make by stainless steel, no ware out during the operation time.

- Galvanize and namplate must follow IEC 60380-1 standard,

- Insulator will be designed which are easily for checking, cleanning and fixing. Technical of insulator must stable during operation time on the power transmission grid. All equipment will be designed for making sure that they are always good on the environments condition where they put on and some case when occur the accident or the fault of system and short circuit.

- Electrical technical and mechanical follow the standard on the system line, the minimum creepage distance must follow Viet Nam standard (11TCN-19-2006, part II) and IEC 60815 standard.

### Requirements for testing

### Type test

- Type test use for checking the basic characteristics of the insulator, which depend mainly on the technical design. These tests are usually done on a small number of insulator and only once which are new design or new manufacturing process, and then repeated only if there is a change in the design or manufacturing process. If the change affects only certain properties, the tests will be done again on those properties. In addition, type tests for electrical, mechanical and thermal-mechanical are not required on new designs of insulation if a valid test certificate is available for insulation which equivalent design and same manufacturing process.

- Type tests according to IEC and standards equivalent standards, including the following content:

1. Type test for Insulators

- Verification of the dimensions, according to IEC 60383-1 standard.

- Dry lighting impulse withstand voltage, according to IEC 60383-1 standard.

- Wet Power frequency withstand voltage, according to IEC 60383-1 standard.

- Electromechanical failing load test, according to IEC 60383-1 standard (for porcelain).

- Mechanical failing load test, according to IEC 60383-1 standard (for glass).

- Thermal-mechanical performance test, according to IEC 60383-1 standard.

- Residual strength test, according to IEC 60797 standard.

- Impulse voltage puncture test, according to IEC 61211 standard.

- Artificial pollution test, according to IEC 60507 standard.

2. Type test for Insulator Sets

- Type test for String insulator sets complete (including insulator + accessories fully assembled), include items:

- Corona test, according to IEC 61284 standard.

- Radio interference test, according to IEC 60437 and 61284 standard.

- Dry lightning impulse withstand voltage test, according to IEC60383-2 standard.

- Wet power frequency withstand voltage test, according to IEC 60383-2 standard.

- Power arc test, according to IEC 61467 standard.

- Mechanical failing load test, according to IEC 61284 standard.

- The type test shall be performed at the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025 standard.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must carry on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, address, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025, (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

- All tests have to fully demonstrate the responsiveness of the equipment offer by bidder. The contractor may be rejected if does not meet the above requirement.

### Routine test

- This test is normal checking for complete products. Routine test reports make by manufacture on each product which are made at the Factory to removing the fault unit. This type test reports shall comply with requiremens according to IEC 60383-1, include the tests below:

- Routine visual inspection.

- Routine mechanical test.

- Routine Electrical test.

- All this test must be confirm and take mark on each complete product.

### Sample test

1. Sample test for Insulators

- Sample testing is carried out in order to check for properties may change during manufacturing process and quality of insulating materials. Sample test is used as acceptance test on insulation samples that are taken random from the batch of goods which satisfied all requirements of routine test.

- This tests verify technical and quality of insulator. This test will check on some insulator (random) which are on the batch of goods and they are already routine test.

- The sample test must be performed according to TCVN 7998-1:2009, IEC 60383 or equivalent standards.

- After the steps of routine testing have passed, the test of components of the insulation shall be tested as follows:

- Verification of the dimensions

- Electro-mechanical failing load test (for porcelain)

- Mechanical falling load test (for glass)

- Verification of the locking system

- Temperature cycle test (for porcelain)

- Thermal shock test (for glass)

- porosity test (for porcelain)

- Puncture withstand test.

- Galvanizing test

- Splice moving checking.

2. Sample test for Insulator sets

- For project with tender package for supplying materials and equipment, which is sets of insulator (including insulators + accessories fully assembled), in order to ensure the quality of equipment provided, the unit assigned to represent the investor is responsible for considering and deciding whether to test samples for set of insulator to ensure satisfy the requirements when it is put into operation. The sample test for set of insulator comply with TCVN, IEC or equivalent standards, including items:

- Dry lightning impulse withstand voltage test, according to IEC60383-2 standard.

- Wet power frequency withstand voltage test, according to IEC 60383-2 standard.

- Power arc test, according to IEC 61467 standard.

- Bidder is responsible for carrying out the sample test during the performance of the contract, when the goods are accepted for acceptance, the contractor must provide a sample test report that is correct with the product supplied for the project.

- The number of samples of insulator chains is selected for testing, the units in collaboration with Engineering of this project will propose at least 02 complete sets of insulator chains representing the shipment provided for the project, including 01 single/double suspention insulator set and 01 double/single tension insulator set.

- In case there is already a Type test (Type tets) for a set of accessory insulators that are correct for the product of the project, then it can be considered to accept without doing (post-test) Sample test (type test for insulator sets are correct for the product of the project: same insulator type, same fittings component, same manufacturer of insulators, fittings of insulator set offered).

- In case the Type tets for a set of accessory insulators are not consistent with the product supplied for the project, the sample test must be considered (post-test) in accordance with regulations.

- For cases of purchasing a small number of accessory insulator string sets for line repair, line connection, and transformer station connection with a variety of types and quantities of 200 string sets of each type or less, PMBs can consider accepting without having to perform a Sample test and the contractor must commit to ensuring the quality of the products included in the project.

- The sample test of insulator strings shall be performed at the independent testing laboratories (domestic or international) in accordance with ISO/IEC 17025 certificate, implement and issue test reports according to the above standards.

- Witnessing test confirmation by the buyer (if necessary) depending on each project is decided by the representative of the investor and agreed upon during contract negotiations.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) Test results must be witnessed and confirmed by independent laboratories certified to ISO/IEC 17025.

Notes: All type test have full demonstrated the responsiveness of the equipment offered by bidders. The Bidder will be rejected if does not meet the above requirements

### Other technical requirement

- Insulator disc when use to install a complete string must be test, include the part according to IEC 60383-2, IEC 61467, IEC 60437 or equivalent.

- When carry out the equipment contract for project, insulator string contractor base on bidding technical requirements and caculate and supply detail caculation table of arcing horn distance for the contruction purposes.

### Requirements for packing

- All packing use to pack the good must have clearly information: total weight, center of load… and heve the sign of regular vouchers.

- All of good must pack carefully then they can move by seaway, airway, railway, overland and make sure that the insulator is protected against bad weather conditions during the transport or storage.

- Each packing has a list with information about materials on the packing and the list will be put on the water-roof envelope. All good will register for easily checking purpose.

### Requirements for transporting

- During transporting, the good must packed with each wood packing which are designed for damage preventting cause by clash. The good must be fasten by rope and avoid the shake down.

### Requirements for Maintenance

- Insulator must pack on a wood packing or arrange on iron support and storage on a private store.

- When arrange insulator do not throw them.

- On the construction site, if do not install the insulator then they will keep on a store. Put them on wood packing or arrange each insulator together and put upper the floor 5-10cm

### Requirements for documents

- Manufacturer information, summary of insulator specifications, origin of insulator, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, structural details drawings and accessories drawings.

- Instructions documents for transortation installation, operation and maintenance of insulator.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

### Other requirements

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

### 500kV, 220kV String Insulator

- Refer to Technical Data Sheet to have data of 500kV, 220kV String Insulator.

## Fittings

### General requirements

- Technical specifications of fittings comply with the provisions of Decision No. 1769/QĐ-HĐTV dated 9/9/2025.

- Fittings are designed for outdoor use, suitable for operation in wet tropical climates, coastal areas, hoarfrost, industrial pollution areas, regions pollution caused by chemicals used in agriculture, snow-covered low temperature areas, areas with large thunderstorms.

- Fittings are designed, tested, manufactured and manufactured using materials and technologies that ensure to meet the standards and standards of Vietnam, the electricity industry, IEC and compliance. suitable for the climate of Vietnam.

### Applicable codes and standards

[1] IEC 61284 (1997-09): Overhead power lines - Overhead lines - Requirements and tests for Fittings.

[2] IEC 61854 (1998-09): Aerial power lines - Overhead lines - Requirements and tests for spacers.

[3] IEC 61897 (1998-09): Overhead lines - Requirements and tests for Overhead lines - Requirements and tests for Stockbridge type aeolian vibration dampers.

[4] IEC 60120 (1984-01): Dimensions of round ends and single junctions of single insulation.

[5] IEC 60372 (1984-01): Connection for single and round ends Amendment Nr.1 ​​(1991-09): Insulated chains - Dimensions and testing.

[6] IEC CISPR / TR 18-3 Ed.3.0en 2017: Radio interference properties of overhead lines and high-voltage equipment. Part 3: Technical process to minimize radio waves.

[7] BS 729: 1971: Hot-Dip Galvanized Coating on Ion & Steel Articles standard

[8] Decision No. 32/QĐ-HĐTV dated 04/02/2025 on the promulgation of the Operation and Maintenance Procedure for 220kV and 500kV Overhead Transmission Lines of the Members’ Council of EVNNPT.

[9] Decision No. 20 / QD-EVNNPT dated March 8, 2018 of the National Power Transmission Corporation on promulgating the Ministry of Procedures for operation and repair.

[10] IEC 60060-1: Kỹ thuật thử nghiệm điện cao áp, Phần 1: Định nghĩa chung và yêu cầu thử nghiệm (High Voltage test Techniques, Part 1: General definitions and test requirement).

[11] IEC 60437 Ed.2: 1997-09: Radio interference test on high voltage Insulators.

[12] IEC/TR 61467 Ed 1.0 2008-08: Insulators for overhead lines with nominal voltage above 1000V-AC. Power arc test on insulator sets.

[13] IEC 60071-1 Ed.8: 2011-03: Insulation co-ordination - Part1: definitions, principles and rules.

[14] IEC 60071-2 Ed.8: 1996-12: Insulation co-ordination - Part2: Application Guide.

### Tension Clamp

Requirements about structure and technical:

- Tension clamp put into operation is the type of outdoor and compression. Each tension clamp include: Aluminium tube for compression Aluminium conductor, Steel tube for compression steel core conductor, Jumper terminal and bolt for tension clamp connecting.

- Aluminium tube for compression Aluminium conductor make by aluminium or aluminium alloy with good conductor of electricity, connect to conductor with bolt include screw and nut and tension clamp. Inside of tension clamp have available compound conductor of electricity and antirust and anticorrosive.

- Steel tube for compression steel core conductor make by galvanized with high bearing capacity. Anchor of tension clamp has annular shape or hook and can install with string insulator and is the type of monolithic structure casting (no weld) with steel tube of steel core conductor compression.

- Jumper terminal is monolithic member  include tension clamp and make by aluminium or aluminium alloy with good conductor of electricity, the title of jumper terminal between 0-30o. Jumper terminal make by at least bolt M12 or bolt M14 or bolt M16 (base on design), depends on the type of wire with corresponding wire diameter/section, the surface of Jumper terminal make sure that It good at conductor of electricity and contact. Inside of Jumper terminal have available compound conductor of electricity and antirust and anticorrosive.

- Tension Clamp must suitable with conductor, do not break conductor during the installation process, good at conductor of electricity, do not release Arc and can carry out fault current when have max short current fault.

- Breaking tension of tension clamp after compression not less than 90% minimum breaking tension of ACSR conductor. The resistance of tension clamp after compression is not more than 1,2 time of conductor.

- On each bays of tension clamp must have product sign and main technical information. On each tube must carve inside some information like below:

- Name or logo of manufacture;

- Sign of tension clamp, Jumper terminal;

- Conductor type;

- Sign of Compression area;

- Marked the arrow and show the direction of compression;

- Each tension clamp must include the documents of dimension and detail technical information, Instruction manual of tension clamp and type of compression area.

Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent

Type test

- This test must follow IEC 61284 standard, at least include:

- Mechanical tests;

- Heating cycle test.

- The type test shall be performed and issued by the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must carry on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025, (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

Routine test

- When delivery good, The Contractor must give the buyer the routine test. Routine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Beside of these test, when the tension clamp install with the string insulator then the string insulate must suitable with the string insulator test.

### Spacer Clamp

Requirements about structure and technical:

- The distance between wire of one phase will calculate on the technical design. Manufacturer must supply the caculate table which make by soft-ware on this bidding and must approve by the owner and designer.

- On the body of spacer clamp must have label. The lable required on the datasheet.

Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284, IEC 61854 standard or equivalent

Type test

- This test must follow IEC 61854, 61284 standard, at least include:

- Clamp slip test (IEC 61854);

- Torsional slip test (IEC 61854);

- Clamp bolt tightening test (IEC 61854);

- Corona voltage and RIV test (IEC 61284).

- The type test shall be performed and issued by the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025.

- In the case of the type test performed by the manufacturer, then this lab must: (i) the Lab of manufacturer must comply with ISO/IEC 17025, (ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must cary on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025 (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

Routine test

- When delivery good, The Contractor must give the buyer the routine test. Routine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284, IEC 61854, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Covering layer checking.

### Suspension clamp

Requirements on structure and technical

- The suspension clamp is designed to synchronize with the insulator string to support the wire according to each type of wire as required.

- The suspension clamp is designed and manufactured with specifications to be suitable for each type of AAC conductor, PHLOX wire has the corresponding cross section.

- The suspension clamp should be light and have a structure that reduces vibration. The suspension clamp shall withstand the electromechanical destructive force equivalent to the corresponding supporting insulation sequence. The support lock is constructed as a joint to support the wire. Clamp body can rotate around one axis and this axis coincides with the center of the conductor.

- The Clamp body can rotate at least 45 degrees in the direction of up or down vertically. The suspension clamp should be made of a material that withstands the destructive load corresponding to the insulator string. The Contractor shall ensure that the calculations and designs are in accordance with the corresponding specific wire type and ensure that in operation, avoid resonance between the Clamp and the conductor or ground wire when being vibrated by the wind.

- Clamp body must be labeled on. The labeling is specified in the Technical specification offered.

Test and inspection

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent

Type test

- This test must follow IEC 61284 standard, at least include:

- Mechanical tests.

- Slip test.

- The type test shall be performed and issued by the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must carry on the product which are same manufacturer and country of manufacture.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025 (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

Routine test

- When delivery good, The Contractor must give the buyer the routine test. Routine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requirement according to IEC 61284, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- In addition to the above tests, when the suspension clamp is assembled synchronously with the insulator string, it is required to test the insulator string as prescribed.

### Fittings of string insulator

Requirements about structure and technical:

- String insulator include some component like below:

- U bolt

- Ball eye

- Arcing horn

- Socket tongue

- U shackle

- Tension clamp

- Suspension clamp

- Insulator

…

- Technical requirements and testing of Tension clamp and Suspension clamp must follow item Tension clamp and Suspension clamp

- Technical requirements and testing of  Insulator must follow item Insulator Strings

- All accessories of string insulator which are supply by contractor must design and make as the same thing on the drawings and requirements of bidding.

- Manufacture must supply calculate table of technical design, design drawings which show the technical requirements of bidding and must approve by the owner and designer.

- Spit pin should make by stainless steel.

- All accessories of string insulator must hot deep galvanized steel follow BS 729 standard or equivalent.

- The surface of zinc coated must flat, clean, and uniform thickness and no fault.

- The arcing horn and arcing ring must design for string and conductor protecting when the electric discharge occur.

- The arcing horn designed with heatproof capability at 600oC of short circuit fault. The arcing horn make sure that in the normal condition they have not arcing on the string and do not make the wave interference.

- On the body of spacer clamp must have label. The lable required on the datasheet.

Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent

Type test

- This test must follow IEC 61284 standard, at least include Mechanical tests and requirements, test items according to table 1 - IEC 61284 (Table 1- Tests on fittings).

- The type test shall be performed and issued by the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must cary on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025, (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

Routine test

- When delivery good, The Contractor must give the buyer the routine test. Routine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requirement according to IEC 61284 and equivalent standards, at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Zinc coated checking.

+ And requirements, test items according to table 1 - IEC 61284 (Table 1- Tests on fittings).

Sample test

- This test must follow IEC 61284 standard, at least include Mechanical tests and requirements, test items according to table 1 - IEC 61284 (Table 1- Tests on fittings). The price is included in the bid price.

a) Insulator set fittings Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Hot dip galvanizing.

- Mechanical tests - damage and failure load.

b) Suspension clamps Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Hot dip galvanizing.

- Mechanical tests - damage and failure load.

- Slip test.

- Clamp bolt tightening test

c) Tension joints and tension clamps Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Hot dip galvanizing.

- Clamp bolt tightening test.

- Tensile test.

d) Partial tension fittings Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Hot dip galvanizing.

e) Repair sleeve Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Tensile test.

f) Insulator protective fittings Sample test including items:

- Visual examination.

- Dimensional and material verification.

- Hot dip galvanizing.

Other requirements:

- Galvanizing shall be performed in accordance with ISO standard or BS 729 or equivalent and apply for hot deep galvanizing process to gain the thickness not less than 610g/sp.m on the surface of steel pad... the coating thickness at saw-tooth will be 305g/sq.m

Requiements for packing

- All of good must pack carefully then they can move by seaway, airway, railway, overland and make sure that the insulator is protected against bad weather conditions during the transport or storage.

- All packing use to pack the good must have clearly information: total weight, center of load… and heve the sign of regular vouchers.

- Each packing has a list with information about materials on the packing and the list will be put on the water-roof envelope. All good will register for easily checking purpose.

- Informations on the packing list must include:

- Type, product sign;

- Total weight;

- Manufacture;

- Year of manufacture;

- Name of project, contruction;

- Hook Place

Requirements for transporting

- During transporting, the good must packed with each wood packing which are designed for damage preventting cause by clash. The good must be fasten by rope and avoid the shake down.

Requirements for Maintenance

- Insulator must pack on a wood packing or arrange on iron support and storage on a private store.

- On the construction site, if do not install the insulator then they will keep on a store. Put them on wood packing or arrange each insulator together and put upper the floor.

Requirements for documents

- Manufacturer information, summary of insulator specifications, origin of insulator, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, structural details drawings and accessories drawings.

- Instructions documents for installation, operation and warning on using.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

Other requirements

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

## CONDUCTOR

### General

- The conductors and fittings supplied under this clause include:

    - All Aluminium Conductor (AAC) 1000sqmm.

    - All Aluminium Conductor (AAC) 800sqmm.

    - All Aluminium Conductor (AAC) 630sqmm.

    - Lightning wires (Phlox 116)

    - AC-XLPE 2.5/PVC – 300mm2

### Requirements on structure and composition of materials

- Surface texture: The surface is uniform, the braids do not overlap, break or break as well as other defects that are harmful to the use process. At the ends and ends of the conductors, there must be cable caps or anti-twist belts.

- Twisted layers: The successive layers of helix must be opposite to each other and tightly twisted together, the outermost twisted layer in the right direction.

- Joints: During the braiding process, it is possible to connect broken aluminum wires, but the joints must comply with the provisions of IEC 61089. The joints must be welded by electric welding and then cold pressing. No joints are allowed on the wires of the steel core.

- The conductor (conductive part) consists of many small aluminum wires twisted around the core.

### Requirements on origin and quality of raw materials

- Information regarding the origin of materials used for conductors must be clearly identified:

- Aluminum:

- Use aluminum ingots or use standard 9.5mm aluminum thread.

- Origin of imported aluminum (Manufacturer's name and address). Requirements for Suppliers of Aluminum Ingots to have a quality registered aluminum mark on the London Nonferrous Metals Exchange (LME registered).

- Before manufacturing, the manufacturer must present all legal documents proving the origin of imported materials.

- Aluminum ingot:

- Minimum aluminum content: 99.7%

- Maximum steel content : 0.2%

- Maximum Si content : 0.1%

- Other ingredients:

- Aluminum thread 9.5 mm .

- Minimum Conductivity : 61.3%

- Breaking stress : (70 -170) N/mm2

- Elongation : (2 -18)%

          - Basic Data of conductor

- All Aluminium Conductor (AAC) 1000sqmm: Refer to Technical Data Sheet to have data of Aluminium Conductor.

- All Aluminium Conductor (AAC) 630sqmm: Refer to Technical Data Sheet to have data of Aluminium Conductor.

### Test and inspection

- Conductor testing shall meet the requirements of IEC 61089, IEC 61395, TCVN 8090:2009 or equivalent standards.

- The tests must be conducted and issued or witnessed by an independent laboratory. These laboratories must be certified to comply with the prescribed standards.

- A type test record must be made on each type of conductor of the batch of products supplied under the contract and with the same manufacturer, country of manufacture.

- Type test report shall include the following information: (i) Name, address, signature/stamp of laboratory; (ii) Tested product, tested items, applied standards, client, date of test, date of publishing, test location, test details, test method, test result,…; (iii) Type, manufacturer, country of tested product.

          - Type test

- The type test record is made by an independent testing laboratory on each product similar to the product according to the design requirement of bidding documents to prove the suitable between required product and the designed product.

- Type test report: The Bidder must provide a Type test report for the conductor according to the bidding documents; The testing laboratory must be an independent and legally unit. Legally testing unit is a unit with testing function as prescribed and independent from organization, financially independent of manufacturers and suppliers.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

- Test records must conform to IEC, TCVN or equivalent standards. The test covers the following main contents:

- Breaking strength of conductor according IEC 61089

- Stress-strain curves according IEC 61089

- Creep Test

- Joints in aluminium wires accoring  IEC 61089;

### Requirements Packaging and label

- Conductors (cables) will be placed in rollers with steel frames. Each type of cable will be wound on an independent roller. The outer diameter of the roller shaft must be large enough to avoid bending and damaging the conductor during winding or pulling.

- The frame of the roller must be sturdy enough to avoid damage to the conductors during transportation and handling. The conductor arm must have a cover plate and other ancillary parts to protect the cable during transportation as well as storage in the warehouse. Nails and other metal sharp objects used to close the spokes of the roller surface must not cause damage to the conductor.

- The ends of the conductors must be sealed with a seal or with a belt that does not allow the ends of the conductors to open. When winding conductors to the roller, the ends shall be fixed to the drum (conductor plate) of the roller. There is a cover that protects the outermost layer of the conductor arm, which cannot be removed until the conductor is installed.

- The conductor arm must be filled information  follow:

- The conductor arm must be filled with the following information

- Type and size of conductor

- Lead length (m)

- Total weight

- Number of lead wires

- Manufacturers Name

- Year of manufacture

- Project name and number

- Arrows determine the direction of rotation of the conductor

- The position of the hook to tie the load-bearing bridge

- Identification marks associated with appropriate transport documents

### Requirements for transpostation

- When shipped, they must be packed in each finished roll and placed in the correct direction according to the manufacturer's instructions. Packages must be secured with ropes to avoid shaking and shifting during transportation.

### Requirements for preservation

- Conductors are packed in rollers, stacked right on the load-bearing ground with self-spreading pads and stored in warehouses or covered yards.

- When loading and unloading, arrangements are not allowed to toss, roll, use cranes or forklifts and secure the ropes.

### Requirments for document

- Information about the manufacturer, summary table of conductor parameters, origin, quality management certificate.

- A valid ISO quality control certificate from the conductor manufacturer is available upon request.

- Must have enough test records

- General drawings with dimensions, section drawings, structural drawings, detailed drawings of related structures of conductors

- Documentation for transportation, installation, operation and maintenance of conductors

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements

- The requirement are not mentioned in this document, it shall apply with TCVN, IEC standard or equivalent.

## ALUMINUM TUBE

### Applicable standard

The Al – tube, end cap and Al corona ball must be made in aluminium alloys according to EN755-2, NEMA 107 and NEMA CC1

### Ratings

- Conductors of E-AlMgSi 0.5F22, annular cross-section, k = 30 m/mm2 at ambient temperature 35oC and conductor temperature 85oC with AC, phase centre-line distance  2 x outside diameter.

- Standard					: ASTM-B317, EN 755-2

- Type						: E-AlMgSi 0,5F22

- Outside diameter				: 160mm

- Inside diameter				: 144mm

- Current carrying capacity			: ≥ 4280A

- Short circuit current 			: ≥ 50kA/1s

### Test

Type test shall be performed and issued by an independent testing laboratory which is accredited to the international standard EN ISO/IEC 17025:2005

The following tests shall be carried out at the workshop:

- Tensile test

- Elongation test

- Resistance measurement

- Electrical characteristics

- RIV and Corona test for Al – tube, end cap and corona ball

- Constructions (dimension).

## HV terminals connectors

### General requirements

- Connectors and terminals for conductors shall be of bolted or compression type as stated in scope of supply, made of high grade aluminium alloy and fitted with bolts of stainless steel or hot-dip galvanized, and suitable for the various size conductors.

- Performances of clamps and connectors shall comply with the following standards: NEMA CC1, IEC 694.

- Connectors for all aluminium conductors, aluminium alloy tubes or equipment designed not to cause corona and radio and audible noise in high-voltage installations up to 500kV.

- Where dissimilar metals are connected, approved means shall be provided to prevent eletcro technical action and corrosion.

- It has ability to carry the rated current that corresponding to the rated current of conductor is connected.

- It has ability to withstand short circuit current as per its equipment.

- The connector for aluminium conductor manufactures with enabling to reduce the corona effect, overheat effect. The surface of clamping plate has to abrade in oder to intensify contacting and treating to connect with other material, do not promote eletcro-chemical effect.

- The bolted plate processed by forged or casting method.

- Bolt and  screw of connector  manufactured  by  stainless steel or hot dip galvanised, including packing ring and auto-lock when fully tightening force, it  guarantee to unloosen bolt by vibration.

- In the body of connector must be show information about devide code and other related information (if any).

- Connector that is submitted by bidder has enough information about ability to carry the rated current, withstand the limited short circuit current, voltage level.

### Contact grease

- Contact grease is required and must be compound including metallic conductive particles which improve the electrical permanent contacts. The compound shall contain an inhibitor of corrosion. The grease protects the metal surfaces against the action of atmospheric oxygen and prevents the formation of oxides which increase the contact resistance.

- Electrical conductivity of contact grease must be less than electrical conductivity of connector.

### Tests

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.23. Required for list of type test reports

- HV Terminal Connectors must be tested by an independent testing laboratory which is accredited to the international standard EN ISO/IEC 17025:2005. The certificate of Accreditation of the laboratory must be submitted as well:

- The following type test reports shall be provided:

    - Temperature rise test.

    - Mechanical tensile test.

    - Short circuit test.

    - Resistance test.

    - Radio Interference Voltage (R.I.V) test.

### Document

- Outline drawings of HV terminals connector/clamp and accessories with dimensions and weights.

- Catalogue of HV terminals connectors/clamps.

- Manual instructions for installation, operation, maintenance of HV terminals connectors/ clamps and accessories.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

## SUPPORT STRUCTURES FOR EQUIPMENT

- Support structures shall be supplied together with all equipment under contract. The Supplier must design and manufacture the support structures in such dimensions that they match the foundations as per drawings of these Bidding Documents. Should for a good reason this not be possible, the Supplier has to inform the Purchaser hereof within latest three months after Contract Signing, indicating the reasons, and including an alternative proposal for the dimensions and arrangement of the fixing points for his structures.

- All support structures for electrical apparatus and equipment in the switchyard shall be galvanised H-shape steel structures as shown in the drawing: EQUIPMENT SUPPORT in this Bidding Document.

- All steel parts must be hot-dip galvanized, quality according to ASTM-123-89a or equivalent. The zinc coating shall be smooth, clean, of uniform thickness of at least 100µm (710 g/m²) and free from defects. The preparation for galvanizing and the galvanizing itself shall not adversely affect the mechanical properties of the coated material. All drilling, punching, cutting and bending of parts shall be completed and all burrs shall be removed before the galvanizing process is applied.

- Screw connections, bolts, etc. are also to be hot dip galvanized in view of the high risk of corrosion, thickness min. 55µm (390 g/m²) including the threaded portions. All nuts shall be galvanized with the exception of the threads, which shall be oiled.

- Materials on which galvanizing damage are detetced after delivery to the construction site, shall be re-dipped unless, in the opinion of the Purchaser or his Representative, the damage is local and can be repaired by applying a coat of galvanizing repair paint. This repair paint must not adversely affect the final coating of the structure.

- Where additional coating is required, galvanized steel must be prepared by chemical treatment before coating. Galvanizing must be exposed to weathering for more than six (06) months prior to coating.

- The Contractor has to guarantee a life-time of the corrosion-protection of at least thirty (30) years (see also BS 5493/1977 Section 2).

- Surfaces shall be visually inspetced. Bare patches, lumps, blisters or inclusions of foreign matter shall be cause for rejection.

- Zinc coating thickness shall be determined non-destructively by an appropriate instrument, however with thickness requirements as per the Contract Specification.

- The zinc coating of all galvanized structure components shall be inspetced and tested in the manufacturer's works according to the following standards:

    - For towers, bolts, screws, rivets, nuts, washers: DIN 50976, DIN 50978, DIN 50981, DIN 267 Part 10 and DIN 50982.

    - Thickness of coating shall be as per General Technical Specifications.

    - The galvanizing tests are to be carried out as sample tests. The sampling rule is to be agreed with the Purchaser.

- Galvanizing Thickness

- The galvanizing thickness shall be tested on site after receiving the galvanized components as well as during erection.  The zinc coatings must comply with the thickness requirements as specified.

- The Contractor shall make available on site for the Purchaser’s use an instrument suitable for the accurate checking of galvanizing thickness. The measuring instrument shall be available from the time of arrival of the first consignment of steelwork until the issue of the taking over certificate.  The cost of the gauge and other operating expenses are deemed to be included in the Contract Price.

- Galvanizing Requirements

- Except where specified to the contrary, all iron and steel used in the construction of the Contract Works shall be galvanized after sawing, shearing, drilling, punching, filling, bending and machining is completed.

- Galvanizing shall be performed in accordance with VDE Standard 0210 (see attachment) or BS 729.

- For galvanizing, only original blast furnace raw zinc shall be applied, which shall have a purity of 98.5%.

- The zinc coating shall be uniform, clean, smooth and as free from spangle as possible. Galvanizing shall be applied by the hot dip process and shall consist of a coating having at least the thickness shown in the table below:

-----------------------------------------------------------------------------------------------

Coating Thickness (Micrometer)

Components	                    No Significant	                    Medium Level

Pollution Areas	                    Pollution Areas

-----------------------------------------------------------------------------------------------

Steel Structures	                              100                                            100

Bolts, Screws, Nuts, Washers          55                                              55

-----------------------------------------------------------------------------------------------

- Steel structure materials shall be treated with Sodium Dichromate or Preton W20 solution after galvanizing to prevent the formation of white rust.

- Bolt, nuts, washers, locknuts and similar hardware shall be galvanized in accordance with the relevant standards. Excess spelter shall be removed by centrifugal spinning.

- Preparation for Galvanizing

- All materials to be galvanized shall be cleaned carefully of rust, loose scale, dirt, oil, grease, and other foreign substances. Particular care shall be taken to clean slag from welded areas.

- The preparation for galvanizing and the galvanizing itself shall not distort or adversely affect the mechanical properties of the material. After galvanizing, holes shall be free from nodules of spelter.

- Repair of Galvanizing

- Material on which galvanizing has been damaged shall be re-dipped unless the damage is local and can be repaired by soldering or by applying a galvanizing repair compound, in this case, the compound shall be applied in accordance with the manufacturer's instructions.

- Soldering shall be done with a soldering iron using 50/50% solder (tin and lead). Surplus flux or acid shall be washed off promptly and the work shall be performed so as not to damage the adjacent coating or the metal itself. Any member on whom the galvanized coating becomes damaged after having been dipped twice shall be rejected.

- If any galvanized part is finally found to be imperfect, it shall be replaced. The whole of the expense involved in the replacement of the imperfect part shall be borne by the Contractor.

- The Contractor shall provide an instrument for checking galvanizing thickness, e.g. Elcometer, or otherwise agree with the Purchaser an approved method of testing galvanizing on Site.

- If, in the opinion of the Purchaser, the extent of damage found on site to a galvanized part appears capable of repair, the Contractor may, after receiving such agreement, attempt to effectively repair by approved methods. The agreement to attempt repair shall not bind the Purchaser to accept the repaired part when this is re-offered for inspection.

- In case it is found that galvanized parts are subject to the formation of white rust or damage resulting from chemical contamination, during shipment or storage on Site, the Purchaser shall either:

- Approve a system of scrubbing and protective painting to be applied on Site, if in his opinion expedient, or

- Forthwith order that the affected parts shall be condemned and that all future shipments shall receive, before dispatch from the Works, special dip or spray treatment to individual members to his approval without extra charge to the Purchaser.

- At least three (03) holes for earthing are on each support structure.

## Required for list of type test reports:

For each type of goods specified in the scope of supply and the detailed technical requirements for each type of goods, the Contractor is required to provide a statistic of the type test reports of the equipment as required in BD (attached with offered) is described in the following table:

LIST OF TYPE TEST REPORTS

| No. | Name of equipment | Manufacture/Country of Origin | Name of Laboratory | Name of Equipment | Name of Test | Dated of test/Nam of code | Standard | Evaluated | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| 1 | Equipment |  |  |  |  |  |  |  |  |

# DATA AND DOCUMENTATION REQUIREMENTS

## General

- Supplier-furnished data and information shall be the guaranteed performance data, predicted performance, interface requirements and construction features of all Supplier’s furnished equipment. The accuracy of such information and its compatibility with overall performance requirements specified by Purchaser are the sole responsibility of the Supplier.

- All information submitted as part of Proposal Data will become part of contract data for successful bidder.

## Data and Information to be submitted with the Bid

- The following data shall be furnished together with the bid:

a.	Filled-in technical data of the Technical Data Sheets.

b.	Preliminary general assembly drawings indicating approximate overall dimensions, cable entrances, weights, nameplates, location of accessories, plans and Section views, mounting and other details and clearances needed for operation and maintenance.

c.	Brochures and catalogues.

d.	Descriptive material, including construction and features of the equipment being proposed.

e.	Typical installation instructions.

f.	Reference list.

g.	Block diagram showing the proposed control scheme.

h.	Technical specification and description of equipment and device to be used.

i.	Control and instrumentation equipment layout.

j.	Brochure and supply experience of manufacturer in supplying relays.

k.	Photographs of similar relays of the type proposed by the Supplier.

l.	A written statement that for all equipment where type tests have been requested, these have been performed successfully and with it a summary of the type test reports.

m.	Shipping splits-approximate weight and size of major pieces.

n.	Supplier shall furnish a list of recommended spare or replacement parts as follows:

1.	Identification (Name of Part).

2.	Replacement time or parameters indicating the need to replace the above.

3.	Unit price of “1” above.

4.	Supplier shall specify the availability and location of spare parts permanently stocked by supplier.

o.	Proposed time schedule to meet delivery date of  protection equipment.

p.	List of test equipment and special tools.

q.	Type test reports summary sheets for the equipment types (or similar type) included in the Bid.

r.	List of codes used.

s. 	Tentative QA Program and ISO Certification.

t.    The commitment of operation lifetime for each offered equipment.

u.  The commitment of defect and failure rate for each offered equipment, and commitment to be at the scene to investigate and determine the cause of defects, failures, and incidents and to remedy if it is due to manufacturer's fault when having the investor’s requirement.

v.  The Supplier complies with the quality management process issued by EVN under the Decision No.01/QD-EVN dated January 03, 2023.

Note:

- All documentaries submitted in the Bid must pursuant to requirement of bidding document;

- All documentaries aimed to prove the qualification and experience of bidder and manufacturer’s capacity, Manufacturer’s authorization letters, Test report, Certificates from realistic end-users for the similar or offered goods or other equivalent documents must be original version or certified regulated copy version.

- To Goods manufactured or processed from abroad, to be imported, the manufacturer has a reason for not being able to submit the original version or a certified true copy of type test report as prescribed when participating in the bid, the Bidder must provide in his bid a written statement from the Manufacturer confirming that the bid document is a photocopy of the original and the Manufacturer commits to be ready to work with the Purchaser to verify the document if is requested.