SECTION III

DESIGN AND PERFORMANCE DATA

- DATA SHEETS OF SUBSTATION

### 500 kV equipment

#### 500 kV Circuit Breakers:

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Ordering number | Stated by Bidder |  |
|  | Applicable standard | IEC 62271-100, IEC 62271-1 |  |
|  | Method of neutral grounding | Directly earthed |  |
|  | Type | Outdoor, Single-pole operation |  |
|  | Insulation environment | SF6 |  |
|  | Voltage specifications: |  |  |
|  | Nominal voltage of system, kV | 500 kV |  |
|  | Maximum operating voltage of system, kV | 550 kV |  |
|  | Rated voltage | 550 kV |  |
|  | Rated frequency | 50 Hz |  |
|  | Rated current | 3150 A |  |
|  | Rated short-time withstand current | ≥ 50 kA rms. |  |
|  | Rated peak withstand current | ≥ 125kA peak |  |
|  | Rated duration of short circuit | ≥ 1 s |  |
|  | Rated Operating Sequence | O-0.3s-CO-3min-CO |  |
|  | Rated lightning impulse withstand voltage: |  |  |
|  | + Phase-to-Earth | 1550 kV peak |  |
|  | + Across the isolating distance | 1550 (+315) kV peak |  |
|  | + Between phases | 1550 kV peak |  |
|  | Rated short-duration power frequency withstand voltage: |  |  |
|  | + Phase-to-Earth | 620 kV |  |
|  | + Across the isolating distance | 800 kV |  |
|  | + Between phases | 620 kV |  |
|  | Rated switching impulse withstand voltage: |  |  |
|  | + Phase-to-Earth | 1175 kV peak |  |
|  | + Across the isolating distance | 900 (+450) kV peak |  |
|  | + Between phases | 1760 kV peak |  |
|  | First-pole-to-clear factor | 1,3 |  |
|  | Minimum creepage distance | ≥ 25 mm/kV |  |
|  | Out of phase breaking current time | ≤ 0,004s |  |
|  | Operating mechanism | Single pole |  |
|  | Operating mechanism drive type | Spring |  |
|  | Minimum clearance between phases | ≥ 7400 mm |  |
|  | Minimum clearance from phase to earth | ≥ 4100 mm |  |
|  | Operating times: |  |  |
|  | - Opening time | < 40 ms |  |
|  | - Closing time | ≤ 120 ms |  |
|  | Rated line-charging breaking current | ≥ 500 Arms |  |
|  | Rated cable-charging breaking current | ≥ 500 Arms |  |
|  | Rated capacitive breaking current | ≥ 400 Arms |  |
|  | DC component of short-circuit breaking current | Stated by Bidder |  |
|  | Resistance of the main circuit | Stated by Bidder |  |
|  | Type of charging | Spring (with charging indicator, charging manually and by motor) |  |
|  | Maximum sound level of Circuit breaker according to IEC 62271-37-082 when operating | Stated by Bidder |  |
|  | On/Off indicator | Yes |  |
|  | Requirements for TRV and RRRV: TRV; RRRV; Short-circuit current. (pu); (kV/μs); (kA-rms). 2,13; 0,50; 37,94. 2,23; 0,55; 22,54. 2,22; 0,66; 12,33. | Comply |  |
|  | TRV peak value of transient recovery voltage |  |  |
|  | + Terminal fault | 817 kV |  |
|  | + Short-line fault | 629 kV |  |
|  | + Out-of-phase | 1123 kV |  |
|  | Rate of rise recovery voltage (RRRV) | To be in accordance with IEC 62271-100 |  |
|  | Mechanical operation duration without maintenance | ≥ 10.000 cycles (closing-opening) |  |
|  | Number of Closing - Opening times at 100% rated current | ≥ 2.500 times |  |
|  | Times of tripping the 50 kA short circuit current | ≥ 10 |  |
|  | Times of tripping the 25kA short circuit current | ≥ 30 |  |
|  | Support insulator |  |  |
|  | Applicable standard | IEC 62155 or equivalent |  |
|  | Materials | Porcelain, brown |  |
|  | Minimum creepage distance | 25mm/kV |  |
|  | Total creepage distance (mm) | Stated by Bidder |  |
|  | Maximum load when operating (kN) | Stated by Bidder |  |
|  | Load withstanding capability of pole, kN | Stated by Bidder |  |
|  | Interrupting chamber system: |  |  |
|  | There shall be devices for dehumidifier, absorbing decomposition substances. Releasing internal high pressure device may be additionally equipped. | Yes |  |
|  | Connection of support insulators; or of other parts is bolts | Yes |  |
|  | Equipotential ring | Yes |  |
|  | Tripping and arc-extinguishing compartment |  |  |
|  | Construction of Arc-extinguishing compartment | Live tank |  |
|  | Quantity of Arc-extinguishing compartment | ≥ 02 |  |
|  | First-pole-to-clear factor, pu | 1,3 |  |
|  | Terminal fault | 1,3 |  |
|  | Short-line fault | 1 |  |
|  | Out-of-phase | 2 |  |
|  | Arc-extinguishing Environment | SF6 |  |
|  | Closing resistor | ≥ 100 Ω |  |
|  | Grading capacitor (installed parallel with chamber) | yes |  |
|  | Quantity of Grading capacitor per one pole | ≥ 2 |  |
|  | Quantity of closing coil per phase | 01 |  |
|  | Quantity of tripping coil per phase | 02 |  |
|  | Number of spare auxiliary contact |  |  |
|  | Normal opening contact | ≥12 |  |
|  | Normal closing contact | ≥12 |  |
|  | SF6 system |  |  |
|  | - Density indicator: |  |  |
|  | + Heat compensation type | Yes |  |
|  | + Quantity: 03 pieces (single-pole circuit breaker) or 01 piece (three-pole circuit breaker) | Yes |  |
|  | + Including warning circuit of SF6 at Level 1 and Level 2. | Yes |  |
|  | - One-way valve for filling and releasing SF6 | Yes |  |
|  | - Loss-rate per year | < 0,5% |  |
|  | - Purity | ≥ 98,5% |  |
|  | - Dew point | Comply with IEC 60376 |  |
|  | - Total mass of SF6 for Circuit breaker | Stated by Bidder |  |
|  | - Rated density of SF6 | Stated by Bidder |  |
|  | - Level 1 density | Stated by Bidder |  |
|  | - Level 2 density | Stated by Bidder |  |
|  | Local control cubicle: |  |  |
|  | - Material of enclosure | Aluminum alloy or stainless steel |  |
|  | - Minimum protection class | IP55 |  |
|  | - Minimum thickness of enclosure | ≥ 2mm |  |
|  | - Local/remote switch | Yes |  |
|  | - Mechanism for opening/closing Circuit breaker | Yes |  |
|  | - Counter | Yes |  |
|  | - Functional circuits (such as monitoring tripping coil circuit, power supply status, spring charging…) | Yes |  |
|  | - Anti-pumping circuit | Yes |  |
|  | - Out-of-phase protection circuit | Yes |  |
|  | - Over-voltage and Overload protection circuit for motor | Yes |  |
|  | - Spring charge indicator | Yes |  |
|  | - Heat system, Led light system, Miniature circuit breaker | Yes |  |
|  | - Charging spring | Manually and motor |  |
|  | - Maximum time for charging | 15s |  |
|  | Auxiliary power supply |  |  |
|  | - Heating and lighting system | 220VAC (+10%; -15%) |  |
|  | - Tripping voltage | 220VDC (+10%; -30%) |  |
|  | - Closing circuit | 220VDC (+10%; -25%) |  |
|  | - Motor for charging spring | 220VDC (+10%; -15%) (it is recommended to equipped additionally the 220VAC (+10%;-15%)) |  |
|  | - Total burden of tripping coils or that of closing coils of three phases | < 1200VA |  |
|  | Steel supporting structure (if any) |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
|  | Terminal connector |  |  |
|  | Materials | Aluminum alloy |  |
|  | Dimension | Suitable for conductor |  |
|  | Bolts for terminal connector | Stainless steel or other suitable materials |  |
|  | Technical documents | English/Vietnamese |  |
|  | Requirements for testing (according to Technical Specification) | Comply |  |
|  | The other specification shall comply with stipulation in Document No. 1677/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT. | Yes |  |

#### 500 kV Dis-connector Switch

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number: |  |  |
| 2.1 | Three-pole Dis-connector with two ES | Stated by Bidder |  |
| 2.2 | Three-pole Dis-connector with one ES | Stated by Bidder |  |
| 3 | Applicable standard | IEC 62271-102 |  |
| 4 | Rated frequency | 50 Hz |  |
| 5 | Neutral system | Directly earthed |  |
| 6 | Type | Outdoor, vertical-break, one-pole, knee type |  |
| 7 | Voltage specification of DS: |  |  |
| 7.1 | Nominal voltage of system | 500kV |  |
| 7.2 | Maximum operating voltage of system | 550kV |  |
| 7.3 | Rated voltage | 550kV |  |
| 7.4 | Rated short-duration power-frequency withstand voltage |  |  |
|  | + Phase to earth | 620 kV |  |
|  | + Across the isolating distance | 800 kV |  |
|  | + Between phases | 620 kV |  |
| 7.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL): |  |  |
|  | + Phase to earth | 1550 kVpeak |  |
|  | + Across the isolating distance | 1550 (+315) kVpeak |  |
|  | + Between phases | 1550 kVpeak |  |
| 7.6 | Rated switching impulse withstand voltage: |  |  |
|  | + Phase to earth | 1175 kVpeak |  |
|  | + Across the isolating distance | 900 (+450) kVpeak |  |
|  | + Between phases | 1760 kVpeak |  |
| 8 | Current specification of DS: |  |  |
| 8.1 | Rated normal current (Ir) | ≥ 3150 A |  |
| 8.2 | Rated short-time withstand current | ≥ 50 kA |  |
| 8.3 | Rated duration of short-circuit | ≥ 1s |  |
| 8.4 | Rated peak withstand current | ≥ 125kA (p) |  |
| 8.5 | Resistance of the main circuit | Stated by Bidder |  |
| 9 | Specification of ES: |  |  |
| 9.1 | Rated short-circuit making current | ≥ 50 kA |  |
| 9.2 | Rated induced current of electrostatic coupling of ES on the line side | 25A rms |  |
| 9.3 | Rated induced current of electromagnetic coupling of ES on the line side | 160A rms |  |
| 9.4 | Rated withstand voltage between insulated terminals and bases earthed | ≥ 635kV |  |
| 10 | Operation ability of DS, ES: |  |  |
| 10.1 | Mechanical structure | Single pole |  |
| 10.2 | Mechanical endurance: |  |  |
| 10.2.1 | DS | M1 class |  |
| 10.2.2 | ES | M0 class |  |
| 10.3 | Quantity of closing/opening times without maintenance: |  |  |
| 10.3.1 | DS | ≥ 2000 |  |
| 10.3.2 | ES | ≥ 1000 |  |
| 10.4 | Crank for manual opening/closing DS and ES | Yes |  |
| 10.5 | Mechanical interlocking structure between DS and ES | Yes |  |
| 11 | Total weight | Stated by Bidder |  |
| 12 | Safety clearance: |  |  |
| 12.1 | Between phases | ≥ 6100 mm (or switching impulse withstand ≥ 1760 kV peak) |  |
| 12.2 | Between phase and earth | ≥ 4100 mm (or switching impulse withstand ≥ 1175 kV peak) |  |
| 13 | Support insulator: |  |  |
| 13.1 | Applicable standard | IEC 60273 or equivalent |  |
| 13.2 | Material | Brown porcelain |  |
| 13.3 | Creepage distance | ≥ 25mm/kV |  |
| 13.4 | Total creepage distance | Stated by Bidder |  |
| 13.5 | Load bearing capability at pole of DS: | Stated by Bidder |  |
| 13.5.1 | For three-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 1,6 (for rated current ≤ 3150A) 2 (for rated current > 3150A) |  |
|  | Cross load (kN) | 0,53 (for rated current ≤ 3150A) 0,66 (for rated current > 3150A) |  |
| 13.5.2 | For one-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 2,0 (for rated current ≤ 3150A) 4,0 (for rated current > 3150A) |  |
|  | Cross load (kN) | 0,8 (for rated current ≤ 3150A) 1,6 (for rated current > 3150A) |  |
| 13.5.3 | Vertical force | 1,5kN |  |
| 13.6 | Maximum load when operating | Stated by Bidder |  |
| 13.7 | Minimum clearance at static state: |  |  |
| 13.7.1 | Between phase and earth | 4100mm |  |
| 13.7.2 | Between 02 poles of 01 phase | 4100mm |  |
| 14 | Materials of main contact | Copper, copper alloy or silver/nickel plated aluminum alloy |  |
| 15 | Mechanical structure: |  |  |
| 15.1 | DS | Motor driver and Manual |  |
| 15.2 | ES | Manual and Motor driver |  |
| 16 | Local control cubicle of DS and ES: |  |  |
| 16.1 | Enclosure | Aluminum alloy or stainless steel (Inox 304) or galvanized steel with suitable paint |  |
| 16.2 | Minimum protection class | IP55 |  |
| 16.3 | Minimum thickness of enclosure | ≥ 2mm |  |
| 16.4 | Normal opening auxiliary contacts of DS | ≥ 12 |  |
| 16.5 | Normal closing auxiliary contacts of DS | ≥ 12 |  |
| 16.6 | Normal opening limit switch contacts of DS | ≥ 3 |  |
| 16.7 | Normal closing limit switch contacts of DS | ≥ 3 |  |
| 16.8 | Normal opening contact of ES | ≥ 10 |  |
| 16.9 | Normal closing contact of ES | ≥ 10 |  |
| 16.10 | Permissible long-term DC current of auxiliary contacts | 10A |  |
| 16.11 | Capability of withstanding the short-term DC current of auxiliary contacts | 100A/30ms |  |
| 16.12 | Remote/Local key switch | Yes |  |
| 16.13 | Opening/closing DS and ES switch | Yes |  |
| 16.14 | Individual auxiliary contacts for power supply of motor and MCBs | Yes |  |
| 16.15 | Over-load and over-current protection for motor | Yes |  |
| 16.16 | Heating system with sensor, led light, MCBs with individual auxiliary contacts for power supply of heating circuit and lighting circuit | Yes |  |
| 16.17 | Electrical interlocking between DS and ES | Yes |  |
| 17 | Operating voltage |  |  |
| 17.1 | Motor driver voltage | 220VDC (+10%; -15%) |  |
| 17.2 | Heating and lighting voltage | 220VAC (+10%; -15%) |  |
| 17.3 | Control of opening/closing DS, ES | 220VDC (+10%; -15%) |  |
| 18 | Steel supporting structure (if any) |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
| 19 | Terminals connector |  |  |
| 19.1 | Materials | Aluminum/copper alloy |  |
| 19.2 | Dimensions | Fit with conductor/bus-bar |  |
| 19.3 | Bolts for terminal connector | Stainless steel or other suitable materials |  |
| 20 | Technical documents | English/Vietnamese |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Document No. 1676/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT | Yes |  |

#### 500 kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60071-1 (2011-03); IEC 60137 (2008-07); IEC 61869-1 (2007-10); IEC 61869 -2 (2012-09); IEC 60529 (2001-02); IEC 60296 (2012-02); IEC 60422 (2013-01); IEC 60028 (1925); IEC 61850-7-3 (2010); IEC 61850-7-4 (2010-03); IEC 61850-6.20 (2009); IEC 61850-6 (2009-12); IEC 61850-9-3 (2016-05); IEC 61869-9 (2016-04) |  |
| 4 | Type | Outdoor, single phase, oil-immersed, Top core, directly earthed |  |
| 5 | Rated voltage | 550 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7.1 | Impulse Voltage (1.2/50s) withstand | 1550 kVpeak |  |
| 7.2 | Switching impulse withstand voltage of primary windings | 1175 kVpeak |  |
| 8 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | 680 kVrms |  |
|  | - Secondary windings | 3 kVrms |  |
| 9 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 10 | Rated Transformation Ratios | 1000-2000-3000-4000/1A |  |
| 11 | Rated Thermal withstand Current | ≥ 50 kA |  |
| 12 | Rated duration of short-circuits | ≥ 1s |  |
| 13 | Rated Dynamic Withstand Current | ≥125 kA |  |
| 14 | Maximum Partial Discharge Level | Comply with IEC 61869-1 |  |
| 15 | Dielectric dissipation factor (tanδ) |  |  |
|  | - Un /3 | Comply with IEC 61869-2 |  |
| 16 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
|  | -Core No. 1 | 1000-2000-3000-4000/1A 15VA - Cl 0.5 |  |
|  | -Core No. 2 | 1000-2000-3000-4000/1A 15VA - Cl 0.5 |  |
|  | -Core No. 3 | 1000-2000-3000-4000/1A 30VA - 5P20 |  |
|  | -Core No. 4 | 1000-2000-3000-4000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 1000-2000-3000-4000/1A 30VA - 5P20 |  |
|  | -Core No. 6 | 1000-2000-3000-4000/1A 30VA - 5P20 |  |
| 17 | Temperature rise limit of windings | 650C |  |
| 18 | Minimum creepage distance | >25 mm/kV |  |
| 19 | Transforming current performed at Secondary winding | Yes |  |
| 20 | Static load-bearing capacity | Comply with IEC 60044-1 and IEC 61869-1 |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Document No. 1819/QĐ-EVNNPT dated 16/09/2025 issued by EVNNPT | Yes |  |

#### 500 kV Capacitor Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60044-2; IEC 60044-5; IEC 61869-5; IEC 60815; IEC 60071; IEC 60137 (2008); IEC 60358-3 (2013) |  |
| 4 | Type | Outdoor, single phase, oil immersed, directly earthed neutral |  |
| 5 | Rated voltage | 550 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7.1 | Impulse Voltage withstand (1.2/50s) | ≥ 1550 kV |  |
| 7.2 | Switching impulse withstand voltage | ≥ 1175rms |  |
| 8 | Power Frequency Voltage withstand at 50Hz, 1 min |  |  |
|  | - Primary windings | ≥ 680 kV |  |
|  | - Secondary windings | ≥ 3 kV |  |
| 9 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,5 (30 seconds) |  |
| 10 | Static load-bearing capability (FR) of high voltage terminal | Stated by Bidder |  |
| 11 | Insulators | Brown porcelain |  |
| 12 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 13 | Voltage ratio, burden, accuracy class |  |  |
|  | + Winding No.1 | 5003/0.113kV; 25VA; class 0.5 |  |
|  | + Winding No.2 | 5003/0.113kV; 50VA; 3P |  |
| 14 | Temperature rise limit of winding | 650C |  |
| 15 | Requirements for testing (according to Technical Specification) | Comply |  |
| 16 | The other specification shall comply with stipulation in Document No. 1816/QĐ-EVNNPT dated 16/09/2025 issued by EVNNPT. | Yes |  |

#### 420 kV Surge Arrester

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacture/Country of Origin | Stated by Bidder |  |
|  | Ordering number | Stated by Bidder |  |
|  | Applicable standard | IEC 60099-4, IEC 60071-1 (2011-03), IEC 60137 (2008-07) |  |
|  | Nominal voltage, kV | 500 |  |
|  | Maximum operating voltage of SA, kV | 550 |  |
|  | Method of neutral grounding | Directly earthed |  |
|  | Type of SA | Outdoor installation |  |
|  | Permissible overvoltage factor for single-phase grounding | 1,4 |  |
|  | Surge arrester connection mode | Phase- earth |  |
|  | Technical specifications of surge arresters |  |  |
|  | Category | Outdoor, ZnO, gapless |  |
|  | Rated voltage (Ur) | 420 kV |  |
|  | Minimum continuous operating voltage (Uc) | 336 kV |  |
|  | Temporary overvoltage with TOV characteristic curve, kVrms |  |  |
|  | - TOV(1s) | ≥ 481 kV |  |
|  | - TOV(10s) | ≥ 447 kV |  |
|  | Nominal discharge current (In) | ≥ 20 kA |  |
|  | Peak discharge current, kApeak | ≤ 100 |  |
|  | Minimum energy absorption capability (Wth) at rated voltage | ≥ 10kJ/kV |  |
|  | Repeated discharge capability - Qrs, C | ≥ 2,4 |  |
|  | Equipotential ring | Yes |  |
|  | Technical specifications of the surge arrester housing |  |  |
|  | Housing materials | Porcelain |  |
|  | Rated short-duration power-frequency withstand voltage | ≥ 680 kV |  |
|  | Rated switching impulse withstand voltage, kV peak | ≥ 1175 kVpeak |  |
|  | Rated lightning impulse withstand voltage (1,2/50 µs-BIL), kV peak | ≥ 1550 kV peak |  |
|  | - Minimum creepage distance | > 25 mm/kV |  |
|  | Rated short-circuit withstand current, kA | ≥ 50kA |  |
|  | Specified long term load, N | ≥ 600 |  |
|  | Specified short term load, N | ≥ 1500 |  |
|  | Mean breaking load, N | ≥ 1800 |  |
|  | Accessories of surge arresters |  |  |
|  | Lightning counter with leakage current display | Yes |  |
|  | Number of digits of the lightning counter | ≥ 5 |  |
|  | Leakage current measurement range, mA | Stated by Bidder |  |
|  | Sensitivity to lightning surge, A | ≤ 200 |  |
|  | Surge current withstand capability (4/10 μs), kA | ≥ 100 |  |
|  | Minimum protection rating of the lightning counter enclosure | IP54 |  |
|  | Steel supporting structure | Galvanized steel with a minimum coating thickness of 80μm |  |
|  | HV terminal: | 01 terminal/ 01 SA |  |
|  | Materials | Compatible with the designed conductors |  |
|  | Dimensions | Compatible with the designed conductors |  |
|  | Bolts of HV terminal | Stainless steel or hot-dip galvanized steel |  |
|  | Accompanying technical documentation clearly showing bid specifications, dimensional drawings, installation instructions, operation guidelines, and maintenance procedures | Yes |  |
|  | Steel supporting structure |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
|  | Leakage current meter shall be capable of communicating with computer control system in control room of substation for online monitoring leakage current. The Bidder shall supply all accessories for connecting and transmitting signals from Leakage current meter to computer control system in control room of substation, such as optical cable, ODF box, optical converter, switching power supply adapter (if any),... | yes |  |
|  | The other specification shall comply with specification in Decision No. 1158/QĐ-EVNNPT dated 27/06/2025 of EVNNPT | yes |  |

### 220 kv equipment:

#### 220 kV Circuit Breakers:

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 62271-100, IEC 62271-1 |  |
| 5 | Type | Outdoor, Single-pole operation |  |
| 6 | Insulation environment | SF6 |  |
| 7 | Rated voltage | 245 kV |  |
| 8 | Rated frequency | 50 Hz |  |
| 9 | Rated current: |  |  |
|  | Type 1 | ≥ 2000A |  |
|  | Type 2 | ≥ 3150 A |  |
| 10 | Rated short-time withstand current | > 50 kA rms. |  |
| 11 | Rated peak withstand current | > 125kA peak |  |
| 12 | Rated duration of short circuit | ≥ 1 s |  |
| 13 | Rated Operating Sequence | O-0.3s-CO-3min-CO |  |
| 14 | Rated Lightning impulse (1.2/50µs) withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | ≥ 1050 kV peak |  |
| 15 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | ≥ 460 kV rms. |  |
| 16 | First-pole-to-clear factor | 1,3 |  |
| 17 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 18 | Out of phase breaking current time | ≤ 0,004s |  |
| 18 | Operating mechanism | Single pole |  |
| 19 | Operating mechanism drive type | Spring |  |
| 20 | Minimum clearance between phases | ≥ 2100 mm |  |
| 21 | Minimum clearance from phase to earth | ≥ 2100 mm |  |
| 22 | Operating times: |  |  |
|  | - Opening time | ≤ 35 ms |  |
| 24 | Rated line-charging breaking current | ≥ 125 Arms |  |
| 25 | Rated cable-charging breaking current | ≥ 250 Arms |  |
| 26 | Rated capacitive breaking current | ≥ 400 Arms |  |
| 27 | DC component of short-circuit breaking current | Stated by Bidder |  |
| 28 | Resistance of the main circuit | Stated by Bidder |  |
| 29 | Type of charging | Spring (with charging indicator, charging manually and by motor) |  |
| 30 | Maximum sound level of Circuit breaker according to IEC 62271-37-082 when operating | Stated by Bidder |  |
| 31 | On/Off indicator | Yes |  |
| 32 | TRV peak value of transient recovery voltage |  |  |
|  | Terminal fault | 364kV |  |
|  | Short-line fault | 280kV |  |
|  | Out-of-phase | 500kV |  |
| 33 | Rate of rise recovery voltage (RRRV) | To be in accordance with IEC 62271-100 and Bidder have to state general capability and full test data. |  |
| 34 | Number of tripping coil | 2 |  |
| 35 | Number of closing coil | 1 |  |
| 36 | Mechanical operation duration without maintenance | ≥ 10.000 cycles (closing-opening) |  |
| 37 | Number of Closing - Opening times at 100% rated current | ≥ 2.500 times |  |
| 38 | Times of tripping the 50 kA short circuit current | ≥ 10 |  |
| 39 | Times of tripping the 25kA short circuit current | ≥ 30 |  |
| 40 | Support insulator |  |  |
|  | Applicable standard | IEC 62155 or equivalent |  |
|  | Materials | Porcelain, brown |  |
|  | Minimum creepage distance | 25mm/kV |  |
|  | Total creepage distance (mm) | Stated by Bidder |  |
|  | Maximum load when operating (kN) | Stated by Bidder |  |
|  | Load withstanding capability of pole, kN | Stated by Bidder |  |
| 41 | Interrupting chamber system: |  |  |
|  | There shall be devices for dehumidifier, absorbing decomposition substances. Releasing internal high pressure device may be additionally equipped. | Yes |  |
|  | Connection of support insulators; or of other parts is bolts | Yes |  |
| 42 | Tripping and arc-extinguishing compartment |  |  |
|  | Construction of Arc-extinguishing compartment | Live tank |  |
|  | Quantity of Arc-extinguishing compartment | 1 |  |
|  | First-pole-to-clear factor, pu | 1,3 |  |
|  | Terminal fault | 1,3 |  |
|  | Short-line fault | 1 |  |
|  | Out-of-phase | 2 |  |
|  | Arc-extinguishing Environment | SF6 |  |
|  | Quantity of closing coil per phase | 01 |  |
|  | Quantity of tripping coil per phase | 02 |  |
| 43 | Number of spare auxiliary contact |  |  |
|  | Normal opening contact | ≥12 |  |
|  | Normal closing contact | ≥12 |  |
| 44 | SF6 system |  |  |
|  | - Density indicator: |  |  |
|  | + Heat compensation type | Yes |  |
|  | + Quantity: 03 pieces (single-pole circuit breaker) or 01 piece (three-pole circuit breaker) | Yes |  |
|  | + Including warning circuit of SF6 at Level 1 and Level 2. | Yes |  |
|  | - One-way valve for filling and releasing SF6 | Yes |  |
|  | - Loss-rate per year | ≤ 0,5% |  |
|  | - Purity | ≥ 98,5% |  |
|  | - Dew point | Comply with IEC 60376 |  |
|  | - Total mass of SF6 for Circuit breaker | Stated by Bidder |  |
|  | - Rated density of SF6 | Stated by Bidder |  |
|  | - Level 1 density | Stated by Bidder |  |
|  | - Level 2 density | Stated by Bidder |  |
| 45 | Local control cubicle: |  |  |
|  | - Material of enclosure | Aluminum alloy or stainless steel |  |
|  | - Minimum protection class | IP55 |  |
|  | - Minimum thickness of enclosure | ≥ 2mm |  |
|  | - Local/remote switch | Yes |  |
|  | - Mechanism for opening/closing Circuit breaker | Yes |  |
|  | - Counter | Yes |  |
|  | - Functional circuits (such as monitoring tripping coil circuit, power supply status, spring charging…) | Yes |  |
|  | - Anti-pumping circuit | Yes |  |
|  | - Out-of-phase protection circuit | Yes |  |
|  | - Over-voltage and Overload protection circuit for motor | Yes |  |
|  | - Spring charge indicator | Yes |  |
|  | - Heat system, Led light system, Miniature circuit breaker | Yes |  |
|  | - Charging spring | Manually and motor |  |
|  | - Maximum time for charging | 15s |  |
| 46 | Auxiliary power supply |  |  |
|  | - Heating and lighting system | 220VAC (+10%; -15%) |  |
|  | - Tripping voltage | 220VDC (+10%; -30%) |  |
|  | - Closing circuit | 220VDC (+10%; -25%) |  |
|  | - Motor for charging spring | 220VDC (+10%; -15%) (it is recommended to equipped additionally the 220VAC (+10%;-15%)) |  |
|  | - Total burden of tripping coils or that of closing coils of three phases | < 1200VA |  |
| 47 | Materials of steel structure (if any) | Galvanized steel |  |
| 48 | Terminal connector |  |  |
|  | Materials | Aluminum alloy |  |
|  | Dimension | Suitable for conductor |  |
|  | Bolts for terminal connector | Stainless steel or other suitable materials |  |
| 49 | Technical documents | English/Vietnamese |  |
| 50 | Requirements for testing (according to Technical Specification) | Comply |  |
| 51 | The other specification shall comply with stipulation in Document No. 1677/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT | Yes |  |

#### 220kV Dis-connector Switch

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number: |  |  |
| 2.1 | Three-pole Dis-connector with two ES | Stated by Bidder |  |
| 2.2 | Three-pole Dis-connector with one ES | Stated by Bidder |  |
| 2.3 | Three-pole Dis-connector no ES | Stated by Bidder |  |
| 2.4 | One-pole Dis-connector | Stated by Bidder |  |
| 3 | Applicable standard | IEC 62271-102 |  |
| 4 | Rated frequency | 50 Hz |  |
| 5 | Neutral system | Directly earthed |  |
| 6 | Type | Outdoor, center-break, three-poles/one-pole, horizontal rotary type |  |
| 7 | Voltage specification of DS: |  |  |
| 7.1 | Nominal voltage of system | 220kV |  |
| 7.2 | Maximum operating voltage of system | 242kV |  |
| 7.3 | Rated voltage | 245kV |  |
| 7.4 | Rated short-duration power-frequency withstand voltage of DS: + Phase-to-Earth + Between phases | ≥ 460 kV |  |
|  | Across the isolating distance | ≥ 530 kV |  |
| 7.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Between phases | ≥ 1050 kV (p) |  |
|  | Across the isolating distance | ≥ 1200 kV (p) |  |
| 8 | Current specification of DS: |  |  |
| 8.1 | Rated normal current (Ir) |  |  |
|  | - For transmission line bays | ≥ 2000 A |  |
|  | - For the other bays | ≥ 3150 A |  |
| 8.2 | Rated short-time withstand current | ≥ 50 kA |  |
| 8.3 | Rated duration of short-circuit | ≥ 1s |  |
| 8.4 | Rated peak withstand current | ≥ 125kA (p) |  |
| 8.5 | Resistance of the main circuit | Stated by Bidder |  |
| 9 | Specification of ES: |  |  |
| 9.1 | Rated short-circuit making current | ≥ 50 kA |  |
| 9.2 | Rated induced current of electrostatic coupling of ES on the line side | 3A rms |  |
| 9.3 | Rated induced current of electromagnetic coupling of ES on the line side | 80A rms |  |
| 9.4 | Rated withstand voltage between insulated terminals and bases earthed | ≥ 283kV |  |
| 10 | Operation ability of DS, ES: |  |  |
| 10.1 | Mechanical structure | Single pole/3 poles |  |
| 10.2 | Mechanical endurance: |  |  |
| 10.2.1 | DS | M1 class |  |
| 10.2.2 | ES | M0 class |  |
| 10.3 | Quantity of closing/opening times without maintenance: |  |  |
| 10.3.1 | DS | ≥ 2000 |  |
| 10.3.2 | ES | ≥ 1000 |  |
| 10.4 | Crank for manual opening/closing DS and ES | Yes |  |
| 10.5 | Mechanical interlocking structure between DS and ES | Yes |  |
| 11 | Total weight | Stated by Bidder |  |
| 12 | Safety clearance: |  |  |
| 12.1 | Between phases | ≥ 2100 mm |  |
| 12.2 | Between phase and earth | ≥ 2100 mm |  |
| 13 | Support insulator: |  |  |
| 13.1 | Applicable standard | IEC 60273 or equivalent |  |
| 13.2 | Material | Brown porcelain |  |
| 13.3 | Creepage distance | ≥ 25mm/kV |  |
| 13.4 | Total creepage distance | Stated by Bidder |  |
| 13.5 | Load bearing capability at pole of DS: | Stated by Bidder |  |
| 13.5.1 | For three-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 0,8 (for rated current ≤ 2500A) 1 (for rated current > 2500A) |  |
|  | Cross load (kN) | 0,27 (for rated current ≤ 2500A) 0,33 (for rated current > 2500A) |  |
| 13.5.2 | For one-phase Dis-connector switch: |  |  |
|  | Straight load (kN) | 1,25 (for rated current ≤ 2500A) 1,6 (for rated current > 2500A) |  |
|  | Cross load (kN) | 0,4 (for rated current ≤ 2500A) 0,5 (for rated current > 2500A) |  |
| 13.5.3 | Vertical force | 1,25kN |  |
| 13.6 | Maximum load when operating | Stated by Bidder |  |
| 13.7 | Minimum clearance at static state: |  |  |
| 13.7.1 | Between phase and earth | 2100mm |  |
| 13.7.2 | Between 02 poles of 01 phase | 2100mm |  |
| 14 | Materials of main contact | Copper, copper alloy or silver/nickel plated aluminum alloy |  |
| 15 | Mechanical structure: |  |  |
| 15.1 | DS | Motor driver and Manual |  |
| 15.2 | ES | Manual and Motor driver |  |
| 16 | Local control cubicle of DS and ES: |  |  |
| 16.1 | Enclosure | Aluminum alloy or stainless steel (Inox 304) or galvanized steel with suitable paint |  |
| 16.2 | Minimum protection class | IP55 |  |
| 16.3 | Minimum thickness of enclosure | ≥ 2mm |  |
| 16.4 | Normal opening auxiliary contacts of DS | ≥ 12 |  |
| 16.5 | Normal closing auxiliary contacts of DS | ≥ 12 |  |
| 16.6 | Normal opening limit switch contacts of DS | ≥ 2 |  |
| 16.7 | Normal closing limit switch contacts of DS | ≥ 2 |  |
| 16.8 | Normal opening contact of ES | ≥ 8 |  |
| 16.9 | Normal closing contact of ES | ≥ 8 |  |
| 16.10 | Permissible long-term DC current of auxiliary contacts | 10A |  |
| 16.11 | Capability of withstanding the short-term DC current of auxiliary contacts | 100A/30ms |  |
| 16.12 | Remote/Local key switch | Yes |  |
| 16.13 | Opening/closing DS and ES switch | Yes |  |
| 16.14 | Individual auxiliary contacts for power supply of motor and MCBs | Yes |  |
| 16.15 | Over-load and over-current protection for motor | Yes |  |
| 16.16 | Heating system with sensor, led light, MCBs with individual auxiliary contacts for power supply of heating circuit and lighting circuit | Yes |  |
| 16.17 | Electrical interlocking between DS and ES | Yes |  |
| 17 | Operating voltage |  |  |
| 17.1 | Motor driver voltage | 220VDC (+10%; -15%) |  |
| 17.2 | Heating and lighting voltage | 220VAC (+10%; -15%) |  |
| 17.3 | Control of opening/closing DS, ES | 220VDC (+10%; -15%) |  |
| 18 | Steel supporting structure (if any) |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
| 19 | Terminals connector |  |  |
| 19.1 | Materials | Aluminum/copper alloy |  |
| 19.2 | Dimensions | Fit with conductor/bus-bar |  |
| 19.3 | Bolts for terminal connector | Stainless steel or other suitable materials |  |
| 20 | Technical documents | English/Vietnamese |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Document No. 1676/QĐ-EVNNPT dated 24/08/2025 issued by EVNNPT | Yes |  |

#### 220 kV Current Transformer

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 61869-2, IEC 60815, IEC 60071, IEC 60137 |  |
| 4 | Type | Outdoor, single phase, oil-immersed, Top core, directly earthed |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7 | Impulse Voltage (1.2/50s) withstand | ≥ 1050 kVpeak |  |
| 8 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | ≥ 460 kVrms |  |
|  | - Secondary windings | ≥ 3 kVrms |  |
| 9 | Capability of withstanding over-current (uninterrupted mode) | >120% of rated primary current |  |
| 10 | Rated Transformation Ratios: |  |  |
|  | Type 1 | 800-1200-2000/1A |  |
|  | Type 2 | 1200-2000-3000/1A |  |
| 11 | Rated Thermal withstand Current | ≥ 50 kA |  |
| 12 | Rated duration of short-circuits | ≥ 1s |  |
| 13 | Rated Dynamic Withstand Current | ≥ 125 kA |  |
| 14 | Maximum Partial Discharge Level | Comply with IEC 61869-1 |  |
| 15 | Dielectric dissipation factor (tanδ) |  |  |
|  | - Un /3 | Comply with IEC 61869-2 |  |
| 16 | Core Characteristics : Ratio, Rated Burden, Accuracy Class |  |  |
| 16.1 | Type 1 |  |  |
|  | -Core No. 1 | 800-1200-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 800-1200-2000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 800-1200-2000/1A 30VA - 5P20 |  |
|  | -Core No. 4 | 800-1200-2000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 800-1200-2000/1A 30VA - 5P20 |  |
| 16.2 | Type 2 |  |  |
|  | -Core No. 1 | 1200-2000-3000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 2 | 1200-2000-3000/1A 10VA - Cl 0.5 |  |
|  | -Core No. 3 | 1200-2000-3000/1A 30VA - 5P20 |  |
|  | -Core No. 4 | 1200-2000-3000/1A 30VA - 5P20 |  |
|  | -Core No. 5 | 1200-2000-3000/1A 30VA - 5P20 |  |
| 17 | Temperature rise limit of windings | 650C |  |
| 18 | Minimum creepage distance | ≥25 mm/kV |  |
| 19 | Transforming current performed at Secondary winding | Yes |  |
| 20 | Static load-bearing capacity | Comply with IEC 60044-1 and IEC 61869-1 |  |
| 21 | Requirements for testing (according to Technical Specification) | Comply |  |
| 22 | The other specification shall comply with stipulation in Document No. 1819/QĐ-EVNNPT dated 16/09/2025 issued by EVNNPT | Yes |  |

#### 220kV Capacitor Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60044- 2; IEC 60044- 5; IEC 61869-5; IEC 60815; IEC 60071; IEC 60137 (2008); IEC 60358-3 (2013) |  |
| 4 | Type | Outdoor, single phase, oil immersed, directly earthed neutral |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Rated frequency | 50 Hz |  |
| 7 | Impulse Voltage withstand (1.2/50s) | ≥ 1050 kV |  |
| 8 | Power Frequency Voltage withstand at 50Hz, 1 min |  |  |
|  | - Primary windings | ≥ 460 kV |  |
|  | - Secondary windings | ≥ 3 kV |  |
| 9 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,5 (30 seconds) |  |
| 10 | Static load-bearing capability (FR) of high voltage terminal | Stated by Bidder |  |
| 11 | Insulators | Brown porcelain |  |
| 12 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 13 | Voltage ratio, burden, accuracy class |  |  |
|  | + Winding No.1 | 2203/0.113kV; 25VA; class 0.5 |  |
|  | + Winding No.2 | 2203/0.113kV; 50VA; 3P |  |
| 14 | Temperature rise limit of winding | 650C |  |
| 15 | Requirements for testing (according to Technical Specification) | Comply |  |
| 16 | The other specification shall comply with stipulation in Document No. 1816/QĐ-EVNNPT dated 16/09/2025 issued by EVNNPT. | Yes |  |

#### 220kV TRV Capacitor

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | Stated by Bidder |  |
|  | Place of factory |  | Stated by Bidder |  |
|  | Designation |  | Stated by Bidder |  |
|  | Applicable standard |  | IEC 60358, IEC 62146-2, IEC 60815, IEC 60071, IEC 60137 |  |
|  | Type |  | Outdoor, single phase, oil immersed, |  |
|  | Rated voltage | kV | ≥245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥1050 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥460 |  |
| - | Secondary windings | kV | ≥3 |  |
| - | Minimum nominal creepage distance | mm/kV | ≥25 |  |
| - | Minimum nominal specific creepage distance | mm | ≥ 6125 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Weight of Intermediate Voltage Transformer | kg | Stated by Bidder |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Capacitance | nF | 20 |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1,2x220kV/√3 |  |
| - | 30 sec |  | 1,5x220kV/√3 |  |
|  | Temperature rise | 0K | 65 |  |
|  | Requirements for testing according to Technical Specification) |  | Yes |  |
|  | Catalogues |  | To be supplied |  |

#### 192kV Surge Arrester

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacture/Country of Origin | Stated by Bidder |  |
|  | Ordering number | Stated by Bidder |  |
|  | Applicable standard | IEC 60099-4; IEC 60071-1:2019; IEC 60137: 2017; IEC 62039; IEC/TS 60815-3 (2008-10); IEC/TS 60815-3 (2008-10) |  |
|  | Nominal voltage, kV | 220 |  |
|  | Maximum operating voltage of SA, kV | 245 |  |
|  | Method of neutral grounding | Directly earthed |  |
|  | Type of SA | Outdoor installation |  |
|  | Permissible overvoltage factor for single-phase grounding | 1,4 |  |
|  | Surge arrester connection mode | Phase- earth |  |
|  | Technical specifications of surge arresters |  |  |
|  | Category | Outdoor, ZnO, gapless |  |
|  | Rated voltage (Ur) | 192 kV |  |
|  | Minimum continuous operating voltage (Uc) | 154 kV |  |
|  | Temporary overvoltage with TOV characteristic curve, kVrms | Stated by Bidder |  |
|  | Nominal discharge current (In) | ≥ 10 kA |  |
|  | Peak discharge current, kApeak | ≤ 100 |  |
|  | Minimum energy absorption capability (Wth) at rated voltage | ≥ 7kJ/kV |  |
|  | Repeated discharge capability - Qrs, C | ≥ 1,6 |  |
|  | Equipotential ring | Stated by Bidder |  |
|  | Technical specifications of the surge arrester housing |  |  |
|  | Housing materials | Porcelain or polymer |  |
|  | Rated short-duration power-frequency withstand voltage | ≥ 460 kV |  |
|  | Rated lightning impulse withstand voltage (1,2/50 µs-BIL), kV peak | ≥ 1050 kV peak |  |
|  | - Minimum creepage distance | > 25 mm/kV |  |
|  | Rated short-circuit withstand current, kA | ≥ 63kA |  |
|  | Specified long term load, N | ≥ 400 |  |
|  | Specified short term load, N | ≥ 1000 |  |
|  | Mean breaking load, N | ≥ 1200 |  |
|  | Accessories of surge arresters |  |  |
|  | Lightning counter with leakage current display | Yes |  |
|  | Number of digits of the lightning counter | ≥ 5 |  |
|  | Leakage current measurement range, mA | Stated by Bidder |  |
|  | Sensitivity to lightning surge, A | ≤ 200 |  |
|  | Surge current withstand capability (4/10 μs), kA | ≥ 100 |  |
|  | Minimum protection rating of the lightning counter enclosure | IP54 |  |
|  | Steel supporting structure | Galvanized steel with a minimum coating thickness of 80μm |  |
|  | HV terminal: | 01 terminal/ 01 SA |  |
|  | Materials | Compatible with the designed conductors |  |
|  | Dimensions | Compatible with the designed conductors |  |
|  | Bolts of HV terminal | Stainless steel or hot-dip galvanized steel |  |
|  | Accompanying technical documentation clearly showing bid specifications, dimensional drawings, installation instructions, operation guidelines, and maintenance procedures | Yes |  |
|  | Steel supporting structure |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
|  | Leakage current meter shall be capable of communicating with computer control system in control room of substation for online monitoring leakage current. The Bidder shall supply all accessories for connecting and transmitting signals from Leakage current meter to computer control system in control room of substation, such as optical cable, ODF box, optical converter, switching power supply adapter (if any),... | yes |  |
|  | The other specification shall comply with specification in Decision No. 1158/QĐ-EVNNPT dated 27/06/2025 of EVNNPT | yes |  |

### 35 kv equipement:

#### 40.5 kV Voltage Transformers

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Ordering number | Stated by Bidder |  |
| 4 | Applicable standard | IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent |  |
| 5 | Type | Outdoor, single phase, 1 or 2 support insulator, oil immersed type |  |
| 6 | Highest operating voltage | 40,5 kV |  |
| 7 | Rated voltage at primary side | 38,5 kV |  |
| 8 | Rated voltage at secondary side | 110/3-110/3 V |  |
| 9 | Neutral type | Isolated |  |
| 10 | Rated frequency | 50 Hz |  |
| 11 | Quantity of secondary windings | 2 cores |  |
| 12 | Voltage ratio, burden, accuracy class |  |  |
|  | + Winding No.1 | 35kV:√3/110V:√3; 10VA; class 0.5 |  |
|  | + Winding No.2 | 35kV:√3/110V:3; 25VA; 3P |  |
| 13 | Impulse Voltage withstand (1.2/50s) | > 185 kVpeak |  |
| 14 | Power Frequency Voltage withstand |  |  |
|  | - Primary windings | > 80 kVrms |  |
|  | - Secondary windings | >3 kVrms |  |
| 15 | Rated voltage factor and rated time: | 1,2 (continuous) |  |
|  |  | 1,9 (8 hours) |  |
| 16 | Maximum Partial Discharge Level at 1,2Um/ 3 |  |  |
|  | Oil immersed | 5 pC |  |
| 17 | Temperature rise limit | 600C |  |
| 18 | Minimum creepage distance | >25 mm/kV |  |
| 19 | Oil level indicator and oil draining valve (for oil-immersed type) | Yes |  |
| 20 | Lid of secondary connection box and lead-sealing position | - Lid of secondary connection box shall be made from aluminum, aluminum alloy, stainless steel or hot-dip galvanized plate steel. - Lid or bottom of box and bolts of lid include holes for lead-sealing. |  |
| 21 | Label of terminals | Label of terminals shall clearly indicate: - Primary and secondary windings; - Parts of windings (if any); - Associated poles of windings and parts of windings; - Intermediate steps (if any). Terminals shall be so clearly marked to be easy detected outside or at vicinity. Label writing shall be performed as follow: - Letters shall be placed after or before numbers, and be capital. - Marks of terminals shall comply with TCVN or relevant IEC standards. |  |
| 22 | Nameplate of VT | Nameplate shall be fixed on VT, and at least contain the followings: - Name of the manufacturer or other signals indicating the manufacturer; - Code and serial number; - Year of manufacturing; - Rated voltage of primary and secondary windings; - Rated frequency; - Rated power and accuracy; - Highest voltage of VT; - Rated insulation level; - Rated voltage factor over operation time; - Insulation class (in case of other than class A). All above information shall not be faded over the years of operation period. |  |
| 23 | Accessories | - Terminals and Terminal connectors at medium voltage shall be made from brass or nickel plated copper to be suitable for designed copper/ aluminum conductor. - Bottom details and bolts shall be hot-dip galvanized or stainless steel. |  |
| 21 | The other specification shall comply with specification in Document No. 104/QĐ-HĐTV dated 21/9/2021 of EVN | Yes |  |

#### 42kV Surge Arrester

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| I | Manufacturer of Surge arrester: |  |  |
| 1 | Manufacture | Stated by Bidder |  |
| 2 | Country of Origin | Stated by Bidder |  |
| 3 | Year of manufacturing | Stated by Bidder |  |
| 4 | Applicable standard | IEC 60099-4 |  |
| II | Specification of transmission grid system: |  |  |
| 1 | Maximum Highest voltage system | 42 kV |  |
| 2 | Rated frequency | 50Hz |  |
| 3 | Neutral type | Isolated earth |  |
| 4 | Voltage factor in case of occurring one-phase earth fault | 1,73 |  |
| 5 | Highest over voltage duration | 7200s |  |
| 6 | Connecting type | Phase – earth |  |
| III | Specification of Surge arrester: |  |  |
| 1 | Type | Outdoor, ZnO, gapless, comply with specification of IEC for surge arrester in substation |  |
| 2 | Class | SL or higher |  |
| 3 | Rated voltage | 51 kV |  |
| 4 | Minimum continuous operating voltage | 42 kV |  |
| 5 | Transient over voltage with curve TOV (kVrms) | Suitable with transmission grid |  |
| 6 | Rated discharge current | 10 kA |  |
| 7 | High current impulse withstand | 100kApeak |  |
| 8 | Minimum energy absorption capability at rated voltage | 4kJ/kV |  |
| 9 | Repetitive charge transfer rating (Qrs) | ≥ 1C |  |
| 10 | Insulation coordination factor | ≥ 1,3 |  |
| IV | Arrester housing: |  |  |
| 1 | Material | Silicon rubber or Porcelain |  |
| 2 | Lightning impulse withstand (1,2/50s) | > 180 kV |  |
| 3 | Power frequency withstand 50Hz/ 1min | > 75 kV (rms.) |  |
| 4 | Minimum creepage distance | > 25 mm/kV |  |
| 5 | Short-circuit withstanding current | > 25kA |  |
| 6 | Static force withstanding | Stated by Bidder |  |
| 7 | Dynamic force withstanding | Stated by Bidder |  |
| V | Accessories: |  |  |
| 1 | Surge counter with leakage current indicator | Yes |  |
|  | Country of origin | Stated by Bidder |  |
|  | Code | Stated by Bidder |  |
|  | Leakage current measuring range | 0 - 30mA |  |
|  | Quantity of digits | ≥ 5 |  |
|  | Sensitivity to lightning impulse | ≤ 200A |  |
|  | High current impulse (4/10s) withstand | ≥ 100kApeak |  |
|  | Protection class | IP54 |  |
|  | Leakage current meter shall be capable of communicating with computer control system in control room of substation for online monitoring leakage current. The Bidder shall supply all accessories for connecting and transmitting signals from Leakage current meter to computer control system in control room of substation, such as optical cable, ODF box, optical converter, switching power supply adapter (if any),... | yes |  |
| 2 | Terminal connectors | 01 piece per 01 surge arrester |  |
|  | Manufacturer | Stated by Bidder |  |
|  | Country of origin | Stated by Bidder |  |
|  | Materials | Suitable with conductor |  |
|  | Dimension | Suitable with conductor |  |
|  | Bolts | Stainless steel or hot-dip galvanized steel |  |
| 3 | Technical documents which clearly indicates offered specification, dimension drawing, instruction manual of installation, operation and maintenance | Yes |  |
| VI | The other specification shall comply with specification in Document No. 110/QĐ-HĐTV dated 21/9/2021 of EVN | yes |  |

### INSULATORS AND FITTINGS

#### 500kV Post Insulator

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60071-1 (2011), IEC 60071-2 (2018), IEC 60168 (2001), IEC 60273 (1990), IEC 60437 (1997), IEC 60507 (2013), IEC 60660 (1999), IEC 60815-1 (2008), IEC 60815-2 (2008), IEC 60815-3 (2008) |  |
| 4 | Type | Outdoor, Brown porcelain, IEC: C10-1550-II |  |
| 5 | Rated voltage | 550 kV |  |
| 6 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 7 | Mechanical |  |  |
|  | - Minimum Failing Load-bending | 10 kN |  |
|  | - Minimum Failing Moment-torsion | 4 kNm |  |
| 8 | Power Frequency Withstand Voltage | ≥ 680 kV |  |
| 9 | Lightning Impulse Withstand Voltage (1.2/50s) | ≥ 1550 kVpeak |  |
| 10 | Switching impulse withstand voltage to earth (250/2500µs). | > 1175 kVrms |  |
| 11 | Puncture voltage | ≥ 1550 kV |  |
| 12 | Dimensions: |  |  |
|  | Height, mm | Stated by Bidder |  |
|  | Diameter, mm | Stated by Bidder |  |
| 13 | Steel supporting structure |  |  |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Material | Hot dip galvanized Steel |  |
| 14 | The other specification shall comply with specification in Decision No. 0103/QĐ-EVNNPT dated 11/7/2019 of EVNNPT | yes |  |

#### 220kV Post Insulator

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60273 |  |
| 4 | Type | Outdoor, Brown porcelain, IEC: C10-1050-II |  |
| 5 | Rated voltage | 245 kV |  |
| 6 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 7 | Mechanical |  |  |
|  | - Minimum Failing Load-bending | 10 kN |  |
|  | - Minimum Failing Moment-torsion | 4 kNm |  |
| 8 | Power Frequency Withstand Voltage |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | ≥ 550 kV |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | ≥ 460 kV |  |
| 9 | Lightning Impulse Withstand Voltage (1.2/50s) | ≥ 1050 kVpeak |  |
| 10 | Puncture voltage | ≥ 1150 kV |  |
| 11 | Minimum phase – earth clearance | 2100 mm |  |
| 12 | Minimum phase – phase clearance | 4200 mm |  |
| 13 | Requirements for testing (according to Technical Specification) | Comply |  |
| 14 | The other specification shall comply with stipulation in Document No. 0103/QĐ-EVNNPT dated 11/7/2019 issued by EVNNPT | Comply |  |

#### 35kV Post Insulator

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacture/Country of Origin | Stated by Bidder |  |
| 2 | Ordering number | Stated by Bidder |  |
| 3 | Applicable standard | IEC 60273 |  |
| 4 | Type | Outdoor, Brown porcelain IEC: C6-170-II |  |
| 5 | Rated voltage | 38,5 kV |  |
| 6 | Minimum creepage distance | ≥ 25 mm/kV |  |
| 7 | Mechanical |  |  |
|  | - Minimum Failing Load-bending | 6 kN |  |
|  | - Minimum Failing Moment-torsion | 1,5 kNm |  |
| 8 | Power Frequency Withstand Voltage |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | ≥ 80 kV |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | ≥ 75 kV |  |
| 9 | Lightning Impulse Withstand Voltage (1.2/50s) | ≥ 180 kV |  |
| 10 | Minimum phase – earth clearance | Stated by Bidder |  |
| 11 | Requirements for testing (according to Technical Specification) | Comply |  |
| 12 | The other specification shall comply with Document No. 0103/QĐ-EVNNPT dated 11/7/2019 issued by EVNNPT | Comply |  |

#### Insulator set:

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacture/Country of Origin | Stated by Bidder |  |
|  | Ordering number | Stated by Bidder |  |
|  | Applicable standard | IEC 60305 |  |
|  | Type of insulator | Outdoor, Toughened glass/porcelain insulator with ball and socket coupling |  |
|  | IEC designation | Type 1: U70BL |  |
|  |  | Type 2: U120B |  |
|  |  | Type 3: U160BL |  |
|  | Type of coupling | Ball and socket |  |
|  | Size of coupling | Type 1: 16mm |  |
|  |  | Type 2: 16 mm |  |
|  |  | Type 3: 20 mm |  |
|  | Minimum breaking strength | Type 1: 70 kN |  |
|  |  | Type 2: 120 kN |  |
|  |  | Type 3: 160 kN |  |
|  | Max nominal diameter of insulating part | Type 1: 255 mm |  |
|  |  | Type 2: 255 mm |  |
|  |  | Type 3: 280 mm |  |
|  | Nominal Spacing | Type 1: 146 mm |  |
|  |  | Type 2: 146 mm |  |
|  |  | Type 3: 170 mm |  |
|  | Min Power Frequency Withstand Voltage: |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | Type 1: 70 kV |  |
|  |  | Type 2: 70 kV |  |
|  |  | Type 3: 75 kV |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | Type 1: 40 kV |  |
|  |  | Type 2: 40 kV |  |
|  |  | Type 3: 45 kV |  |
|  | Dry lightning Impulse Withstand Voltage | ≥ 100 kV |  |
|  | Minimum puncture voltage | 130kV |  |
|  | Minimum nominal creepage distance | Type 1: 295 mm |  |
|  |  | Type 2: 295 mm |  |
|  |  | Type 3: 340 mm |  |
|  | Zinc sleeve on pin | Yes |  |
|  | Weight | Stated by Bidder |  |
|  | Number of insulator per insulator string | N = 25 x 550/L + 2 (500kV) N = 25 x 242/L + 1 (220kV) - N: Number of insulator disc required; - L: Creepage distance per disc offered. - For double insulator set: the number shall be 2xN. |  |
|  | Fixing type to Gantry beam |  |  |
|  | + Type 1 (500kV) | U-bolt, U90 - Ø24, Distance between two rows of bolt holes in a V-shaped string = 3350mm |  |
|  | + Type 2 (220kV) | U-bolt, U90 - Ø24 |  |
|  | Minimum Failing Load-bending (Electromechanical failing load) | Type 1: ≥ 160 kN Type 2: ≥ 120 kN |  |
|  | Requirements for testing (according to Technical Specification) | Comply |  |
|  | The other specification shall comply with stipulation in Document No. 1769/QĐ-EVNNPT dated 09/09/2025 issued by EVNNPT | Comply |  |

Note: The Bidder must calculate the number of insulator string to meet safe clearances.

#### Fittings for insulator set:

| No. | Description | Required | Offered and Guaranteed |
| --- | --- | --- | --- |
| - I | - Fittings for Insulator Sets |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Safety factor | 2,5 |  |
| 5 | All steel fittings are galvanized | Yes |  |
|  | Mass of galvanized layer: | To be Comply with BS 279 |  |
|  | - Fittings, g/sq.m | 610 |  |
|  | - Bolts, nuts and washers, g/sq.m | 305 |  |
| 6 | Material to be used for: |  |  |
|  | - Hinge | Hot-dip galvanized steel |  |
|  | - Ball eyes | Hot-dip galvanized steel |  |
|  | - Ball sockets/socket clevis | Hot-dip galvanized steel |  |
|  | - U-bolts | Hot-dip galvanized steel |  |
|  | - Adjustable extension links | Hot-dip galvanized steel |  |
|  | - Extension links | Hot-dip galvanized steel |  |
|  | - Yoke | Hot-dip galvanized steel |  |
|  | - Bolts and nuts, washer | Stainless steel |  |
|  | - Split pins | Stainless steel |  |
| 7 | Specified mechanical load of fittings, kN | Fit with corresponding insulation set specified in the Bidding documents |  |
| 8 | Information engraved on spacer: Name or logo of the manufacturer + code | Yes |  |
| 9 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| - II | - Arcing horn - Corona ring |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Material to be used for arcing horn | Hot-dip galvanized steel |  |
| 4 | Type of insulation set of conductors: |  |  |
|  | - Tower side | Arcing horn/ Corona ring |  |
|  | - Conductor side | Corona ring |  |
| 5 | Drawings with dimension, installation manual | Yes |  |
| III | Tension clamp |  |  |
| 1 | Manufacturer/ code | - |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Type | Tension set, compressed type with terminal jumper fixed by bolts, used for conductor |  |
| 5 | Compressed shape | Hexagon |  |
| 6 | The offered Tension clamp shall fit with the following conductors: |  |  |
|  | + AAC 630 | Yes |  |
|  | + AAC 800 | Yes |  |
|  | + AAC 1000 | Yes |  |
| 7 | Specified mechanical load of Tension clamp after compressed | ###### ≥ 90% Min. Specified mechanical load of corresponding conductor |  |
| 8 | Resistance of Tension clamp after compressed | ≤ 1,2 times of resistance of conductor with corresponding length |  |
| 9 | Information engraved on Tension clamp: name or logo of the manufacturer + code + conductor type + compressing code + position and direction of compressing | Yes |  |
| 10 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| IV | Suspension clamp |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standards | IEC 61284 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | Type | Suspension clamp type bolts, clamping part shall be fixed by 2 bolts (U shape). Body and clamping part shall be made from aluminum, aluminum alloy or soft steel that is high load-bearing and conductive, corresponding to conductor; or made by hot-dip galvanized load-bearing steel (for TK 70); be capable of resisting deforming and loose status. Surface of suspension clamp shall be so designed to ensure high exposure and conductive |  |
| 5 | The offered Suspension clamp shall fit with the following conductors: |  |  |
|  | + AAC 630 | Yes |  |
|  | + AAC 800 | Yes |  |
|  | + AAC 1000 | Yes |  |
| 6 | Information engraved on Suspension clamp: name or logo of the manufacturer + code + conductor type | Yes |  |
| 7 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |
| V | Spacer |  |  |
| 1 | Manufacturer/ code | Stated by Bidder |  |
| 2 | Applied standard | IEC 61854 or equivalent |  |
| 3 | Quality management standard | ISO 9001:2008 |  |
| 4 | The offered Spacer damper/ Jumper spacer shall fit with the following conductors: |  |  |
|  | + AAC 630 | Yes |  |
|  | + AAC 800 | Yes |  |
|  | + AAC 1000 | Yes |  |
| 4 | Mass of Spacer damper and Jumper spacer | ###### Stated by Bidder |  |
| 5 | Body and clamping part of Spacer damper shall be made from aluminum or aluminum alloy | Yes |  |
| 6 | Bolts, nuts and washers shall be stainless | Yes |  |
| 7 | Information engraved on vibration damper: name or logo of the manufacturer + code + clamping dimension + conductor tye | Yes |  |
| 8 | Technical drawings, catalogue with dimensions, specification and installation manual | Yes |  |

### Conductor

#### All Aluminium Conductor (AAC-800; AAC-630; ACSR-400)

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | Stated by Bidder |  |
|  | Designation |  | Stated by Bidder |  |
|  | Standard |  | IEC 61089 |  |
|  | Type 1 |  | AAC-800 |  |
|  | Type 2 |  | AAC-630 |  |
|  | Type 3 |  | ACSR-400 |  |
|  | Nominal cross section area: |  |  |  |
|  | Type 1 | mm2 | 800 |  |
|  | Type 2 | mm2 | 630 |  |
|  | Type 3 | mm2 | 400 |  |
|  | Stranded number and diameter of strands |  | Stated by Bidder |  |
|  | Type 1 | mm | Stated by Bidder |  |
|  | Type 2 | mm | Stated by Bidder |  |
|  | Type 3 | mm | Stated by Bidder |  |
|  | Stranding direction of outer most layer |  | Stated by Bidder |  |
|  | Type 1 |  | Stated by Bidder |  |
|  | Type 2 |  | Stated by Bidder |  |
|  | Type 3 |  | Stated by Bidder |  |
|  | Minimum strength load |  | Stated by Bidder |  |
|  | Type 1 | kN | Stated by Bidder |  |
|  | Type 2 | kN | Stated by Bidder |  |
|  | Type 3 | kN | Stated by Bidder |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | Stated by Bidder |  |
|  | Type 2 | daN/mm2 | Stated by Bidder |  |
|  | Type 3 | daN/mm2 | Stated by Bidder |  |
|  | Maximum mass of conductor |  |  |  |
|  | Type 1 | kg/km | Stated by Bidder |  |
|  | Type 2 | kg/km | Stated by Bidder |  |
|  | Type 3 | kg/km | Stated by Bidder |  |
|  | Requirements for testing |  | Yes |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C |  |  |  |
|  | Type 1 | A | Stated by Bidder |  |
|  | Type 2 | A | Stated by Bidder |  |
|  | Type 3 | A | Stated by Bidder |  |
|  | Overall diameter of stranded conductor |  |  |  |
|  | Type 1 | mm | Stated by Bidder |  |
|  | Type 2 | mm | Stated by Bidder |  |
|  | Type 3 | mm | Stated by Bidder |  |
|  | Modulus of elasticity of conductor |  |  |  |
|  | Type 1 | daN/mm2 | Stated by Bidder |  |
|  | Type 2 | daN/mm2 | Stated by Bidder |  |
|  | Type 3 | daN/mm2 | Stated by Bidder |  |
|  | DC resistance at 200C |  |  |  |
|  | Type 1 | Ω/km | Stated by Bidder |  |
|  | Type 2 | Ω/km | Stated by Bidder |  |
|  | Type 3 | Ω/km | Stated by Bidder |  |

#### Aluminium Alloy Tube ALMgSi 0.5 TUBE (E-AlMgSi 0.5F22)

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
| 1 | Manufacturer/Country of origin | Stated by Bidder |  |
| 2 | Manufacture’s code | Stated by Bidder |  |
| 3 | Standard | IEC, ASTM-B317, EN 755-2 |  |
| 4 | Type | E-Al MgSi 0.5F22 |  |
|  |  | Ф200/188 |  |
|  |  | Ф160/146 |  |
|  |  | Ф160/150 |  |
| 5 | Outside diameter |  |  |
|  | Type 1 | 200mm |  |
|  | Type 2 | 160mm |  |
|  | Type 3 | 160mm |  |
| 6 | Inner diameter |  |  |
|  | Type 1 | 188mm |  |
|  | Type 2 | 146mm |  |
|  | Type 3 | 150mm |  |
| 8 | Cross-section | Stated by Bidder |  |
| 9 | Mass | Stated by Bidder |  |
| 11 | Continuous current capacity at max. operating temperature of 900C and in air of 250C | Stated by Bidder |  |
| 12 | Short time withstand current | 50 kA/1s |  |
| 13 | Electric DC. Resistance (at 200C) | ≤ 0,01Ω/km |  |
| 14 | Elongation at fracture A5 min. | 8% |  |
| 15 | Minimum breaking load | 215N/mm2 |  |

### HV Connector

| Item No. | Description | Required | Offered |
| --- | --- | --- | --- |
|  | Manufacturer/Country of Origin | Stated by Bidder |  |
|  | Ordering number |  |  |
|  | Applicable standard | IEC 694, NEMA CC1 or equivalent |  |
|  | Type | Aluminum alloy |  |
|  | Surface treatment | The surface of connector must be abraded in order to intensify contacting, and treating in order to prevent corrosion, overheating… |  |
|  | Quantity of Bolt and screw of connector | At least 6 bolts and screw |  |
|  | Continuous current capacity at maximum operating temperature of 900C and in air of 250C |  |  |
|  | - 500kV side | ≥ 3150 A |  |
|  | - 220kV side | ≥ 3150 A |  |
|  | Short-time withstand current |  |  |
|  | - 500kV side | ≥ 50 kA/1sec |  |
|  | - 220kV side | ≥ 50 kA/1sec. |  |
|  | - 35kV side | ≥ 31,5 kA/1sec. |  |
| 13 | Contact grease: | yes |  |
| 15 | Catalogues | To be supplied |  |