[ATTACHMENT 1]

REQUEST FOR PROPOSAL

THƯ MỜI CHÀO GIÁ

Ref: VAPCO/PS-50182-1

To: Potential Bidders

Copy to:

Subject: Supply of Unit 1 minor overhaul services- Lot 1 (BLR/TBN/ELE)/ Cung cấp các dịch vụ tiểu tu Tổ máy 1- Gói 1

- Date: 15 April 2026/ Ngày 15/04/2026

- InstructionS to the participating bidders

Chỉ dẫn đối với các nhà thầu tham gia

  - General information

Thông tin chung

Vung Ang II Thermal Power LLC (VAPCO), the Owner of 2 x 600MW ultra super-critical imported coal-fired thermal Power Plant in Vung Ang Ward, Ha Tinh Province, Vietnam that is being undertaken on a build-operate-transfer basis under Vietnam law, issuing this Request for Proposal (RFP) to invite bidders, who are interested in contracting with VAPCO for the supply of Unit 1 minor overhaul services as detailed in Annex 01.

Công ty TNHH Nhiệt điện Vũng Áng II (VAPCO), Chủ đầu tư Nhà máy Nhiệt điện đốt than nhập khẩu trên siêu tới hạn với công suất 2 x 600MW tại phường Vũng Áng, tỉnh Hà Tĩnh, Việt Nam đang thực hiện dự án xây dựng-kinh doanh-chuyển giao theo pháp luật Việt Nam, ban hành Thư mời chào giá (RFP) này để mời các Nhà thầu quan tâm đến việc ký hợp đồng với VAPCO để cung cấp dịch vụ tiểu tu Tổ máy 1 với mô tả chi tiết như ở Phụ Lục 01.

The service is expected to commence in November 2026.

Dịch vụ dự kiến được bắt đầu trong tháng 11 năm 2026.

  - Compliance with RFP requirements

Tuân thủ các yêu cầu của Thư mời chào giá

The participating bidders shall prepare and submit a Proposal in compliance with the procedures and requirements as outlined in this RFP.  Any omission may give VAPCO a reason to reject or unfavorable evaluation of the Proposal. The participating bidders will be deemed to have fully understood and accepted all the contents of the RFP. Upon submission of a Proposal, the bidders are deemed to have agreed to fully comply with the Contract’s General Terms and Conditions as attached to the RFP.

Các bên tham gia sẽ chuẩn bị và nộp Bản chào tuân thủ các quy trình và yêu cầu như được quy định trong Thư mời chào giá này. Bất kỳ sự sai sót nào có thể khiến VAPCO có lý do từ chối hoặc đánh giá bất lợi cho báo giá. Các bên tham gia sẽ được coi là đã hiểu hoàn toàn và chấp nhận tất cả các nội dung trong Thư mời chào giá. Sau khi nộp Bản chào, khi đó thầu được coi là đã đồng ý tuân thủ đầy đủ các Điều khoản và Điều kiện chính của Hợp đồng như được đính kèm trong Thư mời chào giá.

  - Confidentiality

Bảo mật

The prices in the Proposal must be issued independently, and not be consulted, communicated, or negotiated with any other bidders.

Các giá trong Bản chào của nhà thầu phải được chào độc lập, không được tham khảo, liên lạc hoặc thỏa thuận với bất kỳ nhà thầu nào khác;

The prices stated in the Proposal have not been intentionally disclosed by the bidder and will not be knowingly disclosed, directly or indirectly, to any other participant before the Proposal submission deadline. Furthermore, these prices have not been used, and will not be used, to influence or induce any other person or company to submit, refrain from submitting, or otherwise restrict competition in any way

Các mức giá nêu trong Bản chào chưa từng được nhà thầu cố ý tiết lộ và sẽ không được tiết lộ có chủ đích, trực tiếp hoặc gián tiếp, cho bất kỳ bên tham gia nào khác trước thời hạn nộp Bản chào. Hơn nữa, các mức giá này chưa từng và sẽ không được sử dụng để tác động hoặc lôi kéo bất kỳ cá nhân hay công ty nào nộp, không nộp hồ sơ hoặc hạn chế cạnh tranh dưới bất kỳ hình thức nào.

Participating bidders must not disclose the RFP to any third parties who are not directly involved in the preparation of the Proposal.

Những người tham gia không được tiết lộ Thư mời chào giá cho bất kỳ bên thứ ba nào không liên quan trực tiếp đến việc làm báo giá.

  - Withdrawal of procurement

Thu hồi yêu cầu mua sắm

VAPCO reserves the right, at any time and without any liability to the participants, to cancel, delay or extend this procedure or to change the scope of the procurement.

VAPCO có quyền, bất cứ lúc nào và không có bất kỳ trách nhiệm nào đối với các bên tham gia, trong việc hủy bỏ, trì hoãn hoặc gia hạn thủ tục này hoặc thay đổi phạm vi mua sắm.

  - Language

Ngôn ngữ

The documents shall be prepared in English and Vietnamese. If there is any difference or inconsistency between English and Vietnamese, the English language shall prevail.

Các tài liệu được chuẩn bị bằng tiếng Anh và tiếng Việt. Nếu có bất kỳ sự khác biệt hoặc mâu thuẫn nào giữa tiếng Anh và tiếng Việt thì bản tiếng Anh sẽ được áp dụng.

  - Currency and Payment

Tiền tệ và thanh toán

The price shall be quoted in Vietnamese Dong, exclusive of VAT.

Giá được chào giá bằng đồng Việt Nam, chưa bao gồm thuế GTGT

Payment shall be made in Vietnamese Dong.

Thanh toán được thực hiện bằng đồng Việt Nam.

- Procedures for RFP

Thủ tục mời chào giá

  - Clarification of bidding information

Làm rõ thông tin mời thầu

The participating bidders are requested to study and carefully check the contents of the bidding information and other relevant information. The bidders may send an email to VAPCO’s PIC: Mr. Pham Ngoc Thach, at thach.pham@vapco.com.vn (copying: Mr. Ha Jong Woo, at jeff.ha@vapco.com.vn) or an official letter to VAPCO regarding the unclear contents at least 5 days before the due date of letter of Proposal submission. Written clarifications or feedback via email (as the case may be) will be provided by VAPCO no later than 1 day before the due date of Proposal submission.

Nhà thầu tham gia được yêu cầu nghiên cứu và kiểm tra kỹ lưỡng nội dung của thông tin mời thầu và các thông tin liên quan khác. Các Nhà thầu có thể gửi email cho VAPCO: Ông Phạm Ngọc Thạch theo địa chỉ thach.pham@vapco.com.vn (cc cho ông Ha Jong Woo tại jeff.ha@vapco.com.vn) hoặc thư chính thức đến VAPCO về các nội dung không rõ ít nhất 5 ngày trước ngày hết hạn nộp Hồ sơ chào giá. Giải thích bằng văn bản hoặc phản hồi bằng email (tuỳ trường hợp cụ thể) sẽ được VAPCO cung cấp không muộn hơn 1 ngày hết hạn nộp bản chào.

At any time, before 3 days before the due date of Proposal submission, VAPCO has the right to amend or add to the bidding information. The amendment or supplement shall be communicated in writing to all participating bidders and the bidders shall be obliged to comply with such addition or amendment.

Vào bất kỳ thời điểm nào trước khi hết hạn nộp hồ sơ chào giá 3 ngày. VAPCO có quyền sửa đổi, bổ sung thông tin mời thầu. Việc sửa đổi, bổ sung sẽ được thông báo bằng văn bản tới tất cả các nhà thầu tham gia và các nhà thầu có nghĩa vụ tuân thủ việc bổ sung, sửa đổi đó.

  - Submission of Proposal

Nộp Bản chào

Each bidder will finalize and fill out the form given in Item 4.

Mỗi nhà thầu tham gia sẽ hoàn thiện và điền vào biểu mẫu tại Mục 4.

Bidders are required to submit supporting documents for Technical Evaluation as follows:

- Certificate of business registration

- Reference contracts and completion certificates to supply overhaul services to thermal power plants for the last 7 years

- Work Method Statement inluding detailed overhaul execution plan and heavy equipment and tools deployment plan

- Quality assurance and control plan and procedures

- Risk Assessment Report for technical risk identification and mitigation

- CV of the Project Manager and key engineers showing qualification and overhaul experience

- Detailed schedule at Primavera/ MS Project Level

- Delay Recovery Plan with acceleration strategy

- HSSE Policy, Plan and Procedures

- Safety record showing LTIR/TRIR for the last 3 years

Các nhà thầu phải nộp các giấy tờ chứng minh cho mục đích Đánh giá kỹ thuật như sau:

- Giấy đăng ký kinh doanh của nhà thầu

- Các hợp đồng và chứng nhận hoàn thành tham chiếu cho việc cung cấp dịch vụ kỹ thuật bảo trì cho nhà máy nhiệt điện trong vòng 7 năm qua

- Thuyết minh biện pháp thi công bao gồm kế hoạch triển khai công việc và kế hoạch huy động phương tiện, thiết bị và dụng cụ

- Kế hoạch và quy trình kiểm soát và đảm bảo chất lượng

- Báo cáo đánh giá rủi ro nhằm nhận diện và hạn chế các rủi ro kỹ thuật

- CV của Quản lý dự án và các kỹ sư chính nêu rõ bằng cấp và kinh nghiệm trong tiểu tu

- Bảng tiến độ công việc chi tiết trên nền tảng Primavera/ MS Project Level

- Kế hoạch phục hồi sau gián đoạn với chiến lược tăng tốc

- Chính sách, Kế hoạch và Các quy trình HSSE

- Hồ sơ an toàn bao gồm các thông tin về LTIR/TRIR trong 3 năm qua

Bidders are required to attach a Letter of Confirmation that by submitting the Proposal, they have understood and accepted all major terms and conditions of Part III- Key Terms and Conditions, Annex 01- Scope of Service, and Annex 03- Contract Form of this RFP.

Các nhà thầu phải đính kèm Thư xác nhận rằng bằng việc nộp Thư chào giá, họ đã hiểu và chấp nhận các điều kiện và điều khoản chính của Phần III- Điều kiện và Điều khoản chính, Phụ lục 01- Phạm vi Dịch vụ và Phụ lục 03- Mẫu hợp đồng.

The Proposal Form and other documents shall be submitted by email to the following address no later than the deadline to:

Bản chào sẽ được gửi bằng email đến địa chỉ sau không muộn hơn thời hạn:

Mr. Pham Ngoc Thach / Procurement & Contract Leader,

Vung Ang II Thermal Power LLC,

Address : Vung Ang Economic Zone, Vung Ang Ward, Ha Tinh,

Email: thach.pham@vapco.com.vn,  Phone No: 0986040681,

Copying: Mr. Ha Jong Woo, GA & Contract Manager,

Email: jeff.ha@vapco.com.vn

The Proposal Form will be encrypted to ensure that it won’t be opened before the time specified in Item 3 below.

Bản chào giá sẽ được mã hóa nhằm đảm bảo không được mở trước thời gian quy định trong Điều 3 sau đây.

Email subject: The bidders are kindly requested to clearly state the bidding package’s name and the bidder's name (e.g.: "Proposal for supply of Unit 1 minor overhaul services/ "Bidder's name").

Tiêu đề thư: Nhà thầu ghi rõ tên gói thầu và tên nhà thầu (ví dụ: “Bản chào cho việc cung cấp dịch vụ tiểu tu Tổ máy 1/ "Tên nhà thầu”).

(The bidder may contact Mr. Pham Ngoc Thach for confirmation of the sent email/ Nhà thầu có thể liên hệ với Ông Phạm Ngọc Thạch để xác nhận email đã gửi thành công).

  - Deadline for submission of the Proposal

Thời hạn nộp bản chào giá:

The due date for Proposal submission is 17:00, 07 May 2026

Ngày hết hạn nộp bản chào giá: 17:00, ngày 07/05/2026

The bidder will share the password to open the pdf file of the Proposal Form via email by 09:00, 08 May 2026.

Nhà thầu sẽ gửi mật khẩu để mở Bản chào giá qua email vào 9:00 ngày 08/05/2026.

  - Validity period

Thời hạn hiệu lực

The Proposal shall be offered and valid for 120 days from the due date of Proposal document submission. VAPCO may request to extend the validity time of the Proposal and notify it in writing. The extension time shall not exceed 15 days. If the bidder fails to accept the extension of the validity time, its Proposal will not be considered for evaluation.

Chào giá được đưa ra và có hiệu lực trong vòng 120 ngày kể từ ngày hết hạn nộp hồ sơ chào giá. VAPCO có thể yêu cầu gia hạn thời gian hiệu lực của chào giá và thông báo bằng văn bản, thời gian gia hạn sẽ không vượt quá 15 ngày. Trường hợp nhà thầu tham gia không chấp nhận gia hạn thời gian hiệu lực thì chào giá đó sẽ không được xem xét để đánh giá.

  - Bid evaluation and award criteria

Tiêu chí đánh giá hồ sơ dự thầu và lựa chọn

Proposal evaluation

Đánh giá Bản chào

The bidders' Proposal will be considered and evaluated when they fully meet the above criteria, and the document is submitted as prescribed in Item 2.2 before the deadline or subject to VAPCO’s decision.

Bản chào của Nhà thầu chỉ được xem xét đánh giá khi đáp ứng đầy đủ các tiêu chí nêu trên và nộp bộ hồ sơ như quy định tại Mục 2.2 trước thời điểm đóng thầu hoặc theo quyết định của VAPCO.

- Technical evaluation

Đánh giá về kỹ thuật

- Financial evaluation:

Đánh giá về tài chính

The bidder with the highest combined score from both technical and financial evaluations will be selected as the preferred bidder and invited to enter the contract negotiation stage.

Nhà thầu nào đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính sẽ được chọn vào giai đoạn thương thảo hợp đồng.

- Award Criteria

Tiêu chí lựa chọn

VAPCO will award the Contract to the bidder with the highest combined score from both technical and financial evaluations and favourable terms after negotiation.

VAPCO sẽ ký hợp đồng với Nhà thầu đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính và các điều khoản phù hợp nhất sau khi đàm phán.

VAPCO has the right to adjust the Scope of Service at its discretion.

VAPCO có thể điều chỉnh Phạm vi Dịch vụ theo quyền quyết định của mình.

  - Announcement of evaluation result

Thông báo kết quả đánh giá

The evaluation result might be announced to all participants after the decision on approval of the result. In the notice of the evaluation result, VAPCO is not obligated to explain the reasons for the unsuccessful bidders.

Kết quả đánh giá có thể được thông báo cho các bên tham gia sau khi có quyết định phê duyệt kết quả đánh giá cuối cùng. Trong thông báo kết quả đánh giá, VAPCO không có nghĩa vụ giải thích lý do đối với các nhà thầu không được lựa chọn.

  - VAPCO’s option

Tùy chọn của VAPCO

VAPCO reserves the right, without any liability to the parties, to modify or withdraw this RFP at any time, to increase or decrease the Scope of Service included in the Contract or request to restart the procedure when deemed valid is of the greatest interest to VAPCO and rejects any or all the Proposals. No claim regarding any modification, withdrawal, or restart of the process will be accepted by VAPCO. VAPCO also has the option to award the Contract to an acceptable participant, whichever is in the best interest of the company.

VAPCO bảo lưu quyền, mà không có bất kỳ trách nhiệm nào đối với các bên tham gia, sửa đổi hoặc rút lại Yêu cầu chào giá này bất cứ lúc nào, để tăng hoặc giảm phạm vi công việc được đưa vào Hợp đồng hoặc yêu cầu khởi động lại thủ tục khi được coi là hợp lệ được VAPCO quan tâm nhất và từ chối bất kỳ hoặc tất cả các đề xuất. Không có yêu cầu bồi thường liên quan đến bất kỳ sửa đổi, rút lui hoặc khởi động lại quá trình sẽ được VAPCO chấp nhận. VAPCO cũng có tùy chọn để trao hợp đồng cho bên tham gia chấp nhận được, tùy theo điều kiện nào là tốt nhất cho lợi ích của công ty.

  - Compliance in bidding

Tuân thủ trong đấu thầu

The bidders must comply with the provisions of the law on anti-corruption, anti-bribery, and anti-monopoly and commit to bidding standards to ensure healthy competition, fairness, and transparency.

Các nhà thầu phải tuân thủ các quy định của pháp luật về phòng chống tham nhũng, chống hối lộ, chống độc quyền và cam kết các tiêu chuẩn đấu thầu đảm bảo cạnh tranh lành mạnh, công bằng và minh bạch.

- Key terms and conditions

Điều khoản và điều kiện chính

  - Contract term

Thời hạn Hợp đồng

The Contract shall come into effect upon signing and shall remain in force until both parties have fulfilled their contractual obligations.

Hợp đồng sẽ có hiệu lực kể từ ngày ký và sẽ có hiệu lực cho đến khi hai bên hoàn thành nghĩa vụ theo hợp đồng.

  - Contract price

Giá trị Hợp đồng

The Contract price is based on a fixed-unit price.

Giá trị Hợp đồng được tính trên cơ sở đơn giá cố định.

  - Payment

Thanh toán

Total payment will be made within 30 days from the date of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Proposal form

Mẫu bản chào giá

Bidders are encouraged to submit their Proposals using the following form as per Annex 02.

Nhà thầu được khuyến nghị nộp bản chào theo mẫu ở Phụ Lục 02 sau đây.

Annex 01_ SCOPE OF SERVICE/

PHỤ LỤC 01_ phạm vi DỊCH VỤ

- Scope of overhaul maintenance services for Lot 1 (BLR/TBN/ELE general overhaul)

  - Boiler

| Dept. | Area | No. | Package desription | Work scope (refer next sheet) | Unit | Qtty |
| --- | --- | --- | --- | --- | --- | --- |
| Boiler/ Turbine | BLR/ TBN | 1 | Technical Supervisor | Supervise technical package, prepare all documents | Pack | 2 |
| Boiler | BLR | 2 | Safety Supervisor | Supervise safety for package and prepare PTW | Pack | 1 |
| Boiler | BLR | 3 | High pressure part | Install and dismantle the hydraulic lifting scaffolding system inside furnace; including third-party certification | Pack | 1 |
|  |  |  |  | Remove ash accumulated inside furnace |  |  |
|  |  |  |  | Visual inspection, thicness measurement, hardness test and repair for Pressure part tube (SH, RH, Eco, water wall, slope tube…) Visual inspection for all pressure part: any dent, bending, crack, deformation, abnormality… Measure tube thicness (~23000 points) |  |  |
|  |  |  |  | NDE (replica ~10 points; PT 300-meter length) |  |  |
|  |  |  |  | Build up (welding) for scratches on surface of Slope tube area (~100 points) |  |  |
|  |  |  |  | Clean by grinding & Visual inspection for membrane welding joints of vestibule floor & vestibule side wall (~230 meters) |  |  |
|  |  |  |  | Visual inspection for all headers, snub tube & pipe, roof tube, support & hanger… Cleaning & visual membrane welding of front & side wall (~30 meters) inside penthouse |  |  |
|  |  |  |  | Cut 4 sampling tube of spiral tube, RH, SH tube for analyzing. Re-welding 4 new tube length 500 mm. |  |  |
|  |  |  |  | Depossite Analyzing 4 sampling of boiler tube |  |  |
|  |  |  |  | Visual & repair Boiler insulation, refractory |  |  |
| Boiler | BLR | 4 | FD Fan (Axial Fan 1 stage blade) | Fan: Check for any erosion, corrosion, crack, damage. touch up Check the looseness of anchor bolts of foundation. Repair/ Replace the bellows/expansion joint if needed | Pack | 1 |
|  |  |  |  | Blades inspection: Cleaning and visual inspection of blades for erosion, wearing, damage. Check looseness and tightening torque of blade bolts and rotor assembly bolts. Check gaps between end of blade and casing. Testing vane pitch of blades and doing some adjustment if required. Indication & setting: Tightness check of bolt and nut |  |  |
|  |  |  |  | Blades inspection: PT/ MT test for blades |  |  |
|  |  |  |  | Impeller Inspection: MT/PT test of the welding parts of HBAD support cone (019.081) |  |  |
|  |  |  |  | combined oil: Check for any oil leakage on lubricating, pipeline and vane pitch hyd. control system. Check and replace the spider coupling. Replace oil filter. Replacement of lube oil and cleaning oil tank |  |  |
|  |  |  |  | Motor works ( Fan A) - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | BLR | 5 | CID Fan (Axial Fan 2 stage blade ) | Blades inspection: Cleaning and visual inspection of blades for erosion, wearing, damage. Check looseness and tightening torque of blade bolts and rotor assembly bolts. Check gaps between end of blade and casing. Testing vane pitch of blades and doing some adjustment if required. Indication & setting: Tightness check of bolt and nut | Pack | 1 |
|  |  |  |  | Blades inspection: PT/ MT test for blades |  |  |
|  |  |  |  | Impeller Inspection: MT/PT test of the welding parts of HBAD support cone (019.081) |  |  |
|  |  |  |  | combined oil: Check for any oil leakage on lubricating, pipeline and vane pitch hyd. control system. Check and replace the spider coupling. Replace oil filter. Replacement of lube oil and cleaning oil tank |  |  |
|  |  |  |  | Cooling fan: replace filter; check impeller of 02 fan; check and repair check valve… |  |  |
|  |  |  |  | Motor works ( Fan A) - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | BLR | 6 | PA Fan (Axial Fan 2 stage blade) | Blades inspection: Cleaning and visual inspection of blades for erosion, wearing, damage. Check looseness and tightening torque of blade bolts and rotor assembly bolts. Check gaps between end of blade and casing. Testing vane pitch of blades and doing some adjustment if required. Indication & setting: Tightness check of bolt and nut | Pack | 1 |
|  |  |  |  | Impeller: PT check |  |  |
|  |  |  |  | Blades inspection: Cleaning and visual inspection of blades for erosion, wearing, damage. Check looseness and tightening torque of blade bolts and rotor assembly bolts. Check gaps between end of blade and casing. Testing vane pitch of blades and doing some adjustment if required. Indication & setting: Tightness check of bolt and nut |  |  |
|  |  |  |  | Blades inspection: Visual & surface preparation for PT/ MT test for blades |  |  |
|  |  |  |  | combined oil: Check for any oil leakage on lubricating, pipeline and vane pitch hyd. control system. Check and replace the spider coupling. Replace oil filter. Replacement of lube oil and cleaning oil tank |  |  |
|  |  |  |  | Motor works ( Fan A) - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silical gel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | BLR | 7 | Mill Seal Air Fan | Clean filter, check all fan condition, anchor bolt, touch up | Pack | 1 |
|  |  |  |  | Check coupling alignment, spring pack check & replacement |  |  |
|  |  |  |  | Impeller visual check |  |  |
|  |  |  |  | Inlet vane: Greasing up to bearing Check & correct the inlet vane condition |  |  |
| Boiler | BLR | 8 | Pulverizer | Classifier Check the classifier blade for any erosion and deformation. Check the gap of Classifier rotor and casing. V-belt inspection for any crack, loosen and do the tension, bolt tightening Clean coal accumulation between the classifier rotor and casing. | Pack | 1 |
|  |  |  |  | Gearbox: - Coupling: Shaft alignment checked and plate pack check. Check & tight the loosening of the expansion joint bettwen gearbox and grinding table |  |  |
|  |  |  |  | Replace Oil unit(HPU/LO) filter and oil purifier Cleaning/ Sealing Air Piping cleasing |  |  |
|  |  |  |  | Clean the coal remaining insider Pulverizer, Piryte hopper, seal air pipe... Visual inspection Grinding table and roll tire for ansy erosion, crack, loosen, leaking point Measure the erosion of roller tyre and record it check /adjust gap the roller - grind plate Check and tighten any loose bolts or connections. Check accumulator blade satus and replace if requierd |  |  |
|  |  |  |  | Motor works ( only C & E): - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | BLR | 9 | Coal Feeder | Visual inspection inside of the coal feeder belts, pulley, roller, conveyor, belts scraper blades and repair if needed Inspection the belts driver gear and clean out driver reducer, replace the oil, bearing if required. | Pack | 1 |
|  |  |  |  | Replace belt conveyor if required |  |  |
| Boiler | BLR | 10 | Coal silo | - Visual inspection inside coal silo; - Measure thickness of coal silo wall and liner plater. - Visual inspection inside intermediate chute, expantion joints. - Check the Wear-resistant plate condtion - Check the expantion joint condition | Pack | 1 |
| Boiler | BLR | 11 | Scanner Cooling Air Fan | Clean filter, check all fan condition, anchor bolt, touch up | Pack | 1 |
|  |  |  |  | Check coupling alignment, bearing replacement, spring pack check & replacement |  |  |
|  |  |  |  | Impeller visual check |  |  |
|  |  |  |  | Check coupling alignment, spring pack check & replacement |  |  |
|  |  |  |  | Impeller visual check |  |  |
| Boiler | BLR | 12 | SCR Dilution Air Fan | Clean filter, check all fan condition, anchor bolt, touch up | Pack | 1 |
|  |  |  |  | Check coupling alignment, spring pack check & replacement |  |  |
|  |  |  |  | Impeller visual check |  |  |
| Boiler | BLR | 13 | APH_ Gas Air Heater | Visual for welding joint, Rotor, Rotor core, pin rack, Rotor pivot, pin rack assembly; trunnion bolt… Visual weld joint of sector plate, top casing, middle casing, bottom casing | Pack | 1 |
|  |  |  |  | Guide & support bearing: visual, oil replacement |  |  |
|  |  |  |  | Heat element: visual, weight measurement, loosening & cleaning; recommendation to owner |  |  |
|  |  |  |  | Speed reducer: visual inside/outside & function check, oil & grease replacement |  |  |
|  |  |  |  | Seal frame: visual, thickness measurement, replace rod packing of actuator; visual top & bottom expansion sleeve… |  |  |
|  |  |  |  | Visual water washing device, fire extinguisher, oil circulation system, replace oil filter, cleaning oil cooler. |  |  |
|  |  |  |  | Soot blower: visual & greasing, |  |  |
| Boiler | BLR | 14 | Burner | SA/TA Tube Front check for Thermal Deformation touch up. | Pack | 1 |
|  |  |  |  | Flame Holder Tooth check for erosion; Flame Holder Mounting Pin check |  |  |
|  |  |  |  | Core Air Tube Support Drop out and Abrasion check Primary Air Tube Lining/Casting Abrasion check |  |  |
|  |  |  |  | Oil Burner Primary Swirler Thermal Damage Check |  |  |
| Boiler | BLR | 15 | SCR (Selective Catalytic Reduction) | Check spray nozzle, de-clogging of nozzle, visual check & de-clogging catalyst block. | Pack | 1 |
|  |  |  |  | Take sample of catalyst for analyzing remaining lifetime |  |  |
| Boiler | BLR | 16 | Reheater attemperator | Dismantling (including IC & electrical part) for visual check nozzle, nozzle holder; replace soft part & reinstallation. | Pack | 1 |
|  |  |  |  | Liner inspection: use borescope to check liner distortion/cracking, upstream & downnstream pipe weld. |  |  |
|  |  |  |  | PT for all weld joints. |  |  |
| Boiler | BLR | 17 | Boiler safty valve | Dismantling for 16 PSV & 2 EBV for internal visual inspection; Replace soft part | Pack | 1 |
|  |  |  |  | Seat & disc contact check, lapping. Recover valve seat if damaged |  |  |
|  |  |  |  | Popping & safety certification. |  |  |
| Boiler | BLR | 16 | Boiler Control valve | Dismantle &re- installation (including IC & electrical part, re calibration) 51 control valve for internal visual inspection & cleaning; Replace soft part. Touch up. | Pack | 1 |
|  |  |  |  | Seat & disc contact check, lapping if needed |  |  |
| Boiler | BLR | 17 | Boiler MOV | Dismantle &re- installation (including IC & electrical part, recalibration) 43 MOV valve for internal visual inspection & cleaning; Replace soft part. | Pack | 1 |
|  |  |  |  | Seat & disc contact check, lapping if needed |  |  |
| Boiler | BLR | 18 | Boiler Control Damper | Visual wearing, distortion of blade, gear, linkage bar & greasing, correction bending/crack part for 33 control dampers. | Pack | 1 |
|  |  |  |  | Replace packing for 03 RH dampers, 02 SH dampers. |  |  |
|  |  |  |  | Test running for smooth operation |  |  |
|  |  |  |  | 03 RH dampers, 02 SH dampers: Replace shaft upper bearing. Replace packing at shaft lower. |  |  |
| Boiler | BLR | 19 | Boiler Shut Off Damper | Visual wearing, distortion of blade, gear, linkage bar & greasing. Repair for distortion & crack. 22 Dampers. | Pack | 1 |
|  |  |  |  | Test running for smooth operation |  |  |
| Boiler | BLR | 20 | Gas-Air Duct | Cleaning & visual check wearing, abnormal. Check thickness of duct to check corrosion. | Pack | 1 |
|  |  |  |  | Replace gasket & insulation at manhole |  |  |
|  |  |  |  | visual check for expansion joint |  |  |
| Boiler | BLR | 21 | Flash Tank | Clean & visual check welding joint | Pack | 1 |
|  |  |  |  | Random measure thickness of tank |  |  |
| Boiler | BLR | 22 | SDCC | Visual inspection for Chain link, liner, impact bar, … Visual inspection for crusher (coupling, gear box, segment, ...). Replace flexible segment of coupling | Pack | 1 |
|  |  |  |  | HPU Chain tensioning, SDCC HPU: - Check the internal condition of the facility components for wearing, deposit build up and rust. Replace any worn or damaged components. - Change the oil and clean the oil tank. - Change the filter elements. |  |  |
|  |  |  |  | Roll out and roll in SDCC |  |  |
| Boiler | AHS | 23 | ESP | Check and clean the dust accumulated status inside. | Pack | 1 |
|  |  |  |  | Check the side panels, access doors and insulator compartments on top of ESP to see if there are phenomena of air leakage, condensation, corrosion or dust accumulation, if there are, eliminate them |  |  |
|  |  |  |  | Check the gas distribution screens may have dust accumulations or blockages somewhere due to low gas velocity thereon. Check and clean manually |  |  |
|  |  |  |  | Check the emitting frames and discharge wires to ensure that they are not deformed and that there is no dust deposit. |  |  |
|  |  |  |  | Check the collecting plates and shock bars to ensure that they are not bent and that there is no dust deposit. |  |  |
|  |  |  |  | Check the hammer system and replace if required. Inspection Seal air fan ; impeller, ventilation valve etc. |  |  |
| Boiler | AHS | 24 | Ash handling system | Dome valve ; Visual check, realigment, retighten bolts, lubricating dome valve shaft Bearing, insert seal, replacement if needs | Pack | 1 |
|  |  |  |  | Inspection Air compressor and dryer clean inside of the casing and check the oil condition |  |  |
|  |  |  |  | Inspection Air blower in the silo; V-belt and blower clean inside of the casing and check the oil condition (Repace the oil, filter element and dryer desiccant). |  |  |
|  |  |  |  | Bag filter system ; General check of the fan, outlet butterfly valve, casing, etc., to ensure the system is operating smoothly. Check the filter bag and replace if neccessary |  |  |
| Boiler | FGD | 25 | FGD-GGH | Check and clean the dust accumulated status inside. | Pack | 1 |
|  |  |  |  | Check and adjust/repair of rotor seal thickness (top/bottom) |  |  |
|  |  |  |  | Check of the rotor seal top/bottom for: Missing clamping screws and seat of the connections |  |  |
|  |  |  |  | Heating element: Inspect, clean and repair top and bottom surfaces for foreign matter, fouling, corrosive damage, erosive damage, or loose plates. |  |  |
|  |  |  |  | Inspection of the rotor walls for weld cracks (top/bottom) |  |  |
|  |  |  |  | Check of the rotor flanges for corrosion (top/bottom) |  |  |
|  |  |  |  | General check and repair of the protective coating. |  |  |
|  |  |  |  | Check of the rotor flange for erosion (top/bottom) |  |  |
|  |  |  |  | Check gaskets at all access openings. |  |  |
|  |  |  |  | Examine duct reinforcements for erosive or corrosive damage. |  |  |
|  |  |  |  | Check and repair for wear at the pinion/pin rack and repair if needed. |  |  |
|  |  |  |  | Casing Inspection and repair: Check for erosive/corrosive damage and ensure the mobility of the spring pins. |  |  |
|  |  |  |  | Oil change on the gearboxes and bearing assembly |  |  |
|  |  |  |  | Check condition of sootblowers: change packing, check and repair lance tube, feed tube, poppet valve |  |  |
| Boiler | FGD | 26 | FGD_Oxidation Air Blowers | Replace filters element of: suction filter, oil filter, breather filter | Pack | 1 |
|  |  |  |  | Check if the impeller, inlet Scroll is worn or abraded or cracked. (Check the gap between the inlet scroll and impeller) |  |  |
|  |  |  |  | Clean the impeller, inlet scroll, diffuser. |  |  |
|  |  |  |  | Check the oil passage for foreign matter and flushing |  |  |
|  |  |  |  | Check O-ring and gasket for damage and replace if necessary |  |  |
|  |  |  |  | Check condition of lubrication system components: flushing the oil, piping joint, check valve, oil pressure control (relief) valve |  |  |
|  |  |  |  | Check the mist filter for contamination or clogging. |  |  |
|  |  |  |  | Check the condition of oil heater and oil cooler |  |  |
|  |  |  |  | Check the condition of flexible disc coupling |  |  |
|  |  |  |  | Check the condition of air piping system |  |  |
|  |  |  |  | Motor works (only OAB-B): - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | FGD | 27 | FGD_Absorber Spray Pumps | Check the function of valves and auxiliary piping | Pack | 1 |
|  |  |  |  | Check centering and run-out of shaft |  |  |
|  |  |  |  | Replace lubricant (Grease & Oil) |  |  |
|  |  |  |  | Remove and re-coat anti-seize, thread locker, and rust preventives. Especially those parts immersed in seawater (ex: flange, bolt thread) need to be coated with anti-crevice corrosion sealant. |  |  |
|  |  |  |  | Examine all fasteners (bolt, nut, and washer). If there is any sign of damage such as crack and corrosion, replace it with new one |  |  |
|  |  |  |  | Replace gland packing |  |  |
|  |  |  |  | Motor works ( Only ASP-B): - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. |  |  |
| Boiler | LDO | 28 | LDO_system | Check for any erosion, corrosion, crack, damage. touch up, leakage, check the looseness of bolts… of system's components Clean and check all filters | Pack | 1 |
|  |  |  |  | Transfer pump: Dismantle the pump and check components: shaft, impeller, casing, mechanical seal Replace gasket, oring, oil seal, casing wear ring, bearing Check condition of coupling |  |  |
|  |  |  |  | Forwardeing pump: Check suction casing, discharge casing, stage casing Check mechanical seal, coupling Replace shaft bearings and air release filter |  |  |
| Boiler | BLR | 29 | Boiler Recircutaling Pump motor (500kW) | Motor works: - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Pack | 1 |

  - Turbine

| Dept. | Area | No. | Package desription | Work scope (refer next sheet) | Unit | Qtty |
| --- | --- | --- | --- | --- | --- | --- |
| Turbine | TBN | 1 | Technical Supervisor | Supervise technical package, prepare all documents | Set | 1 |
| Turbine | TBN | 2 | Safety Supervisor | Supervise safety for package and prepare PTW | Set | 1 |
| I | Mechanical Work Scope |  |  |  |  |  |
| TBN | Feedwater System | 1 | Deaerator | 1. Prepare tool, consumable, spare part 2. Remove the manhole 3. Ventilation and hazardous gas testing inside the deaerator 4. Internal inspection for evidence of corrosion, scaling crack or broken or worn parts and check the Spray Valve, Spray Nozzle, repair or replace if necessary. 5. Cleaning inside the deaerator 6. Post-cleaning inspection inside the deaerator 7. Replace the new gasket 8. Close the manhole 9. Leak inspection 10. Inspection report | Set | 1 |
| TBN | Feedwater System | 2 | Feedwater Storage Tank | 1. Prepare tool, consumable, spare part 2. Remove the manhole 3. Ventilation and hazardous gas testing inside the deaerator 4. Internal inspection for evidence of corrosion, scaling crack or broken or worn parts and repair if necessary. 5. Cleaning inside the Feedwater Storage Tank 6. Post-cleaning inspection inside the Feedwater Storage Tank 7. Replace the new gasket 8. Tighten the manhole 9. Leak inspection 10. Inspection report | Set | 1 |
| TBN | Feedwater System | 3 | Boiler Feedwater Booster Pump #A/B | 1. Prepare tool, consumable, spare part 2. Remove the coupling 3. Disassemble the bearing housing, check any damage to the bearings due to any foreign materials, and clean it. Also, clean and check the bearing housing. 4. Check all pipelines, such as the drain lines, the seal water lines, the lubricating oil lines, the cooling water lines and the suction strainers, for clogging 5. If an excessive leakage is found on the mechanical seal during operation, check the mechanical seal. 6. Check each strainer element, in the feed water line, in the seal water line, and in the lubricating oil line. Further clean it completely to remove any foreign materials (Clean the Mech Seal Magnetic Filter A, B; Clean and check the Mech Seal Cooler A,B; Clean the Suction Strainer of BFBP A,B; Clean and check oil cooler) 7. Check the lubricant oil, and if necessary, change it into new oil. 8. Check the alignment, and if necessary, adjust the alignment. 9. Replace the gaskets on the suction and discharge pipe 10. Inspection report | Set | 2 |
| TBN | Feedwater System | 4 | Boiler Feedwater Pump #A/B | 1. Prepare tool, consumable, spare part 2. Remove the coupling 3. Disassemble the bearing housings, check any damage on the bearings due to any foreign materials, and clean it. Also, clean and check the bearing housings. 4. Check all pipelines, such as the drain lines, the seal water lines, the lubricating oil lines, the cooling water lines and the suction strainers, for clogging. It necessary, carry out flushing. 5. Check each strainer element in the seal water line. Further clean it completely to remove any foreign materials 6. Check the alignment, and if necessary, adjust the alignment. 7. Replace the gaskets on the suction and pipe 8. Inspection report | Set | 2 |
| TBN | Feedwater System | 5 | Feedwater Heater No.6 Overhaul | 1. Prepare tool, consumable & spare parts 2. Open the manhole 3. Clean tube of heater with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 3. Check condition of welded joints 4. Tube of heater leak check 5. Prepair/ build-up the welding depends on leak test result. 6. Replace the manhole gasket, partition gasket. 7. Close the manhole 8. Inspection report. | Set | 1 |
| TBN | Feedwater System | 6 | Feedwater Heater No.7 Overhaul | 1. Prepare tool, consumable & spare parts 2. Open the manhole 3. Clean tube of heater with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 3. Check condition of welded joints 4. Tube of heater leak check 5. Prepair/ build-up the welding depends on leak test result. 6. Replace the manhole gasket, partition gasket. 7. Close the manhole 8. Inspection report. | Set | 1 |
| TBN | Feedwater System | 7 | Feedwater Heater No.8 Overhaul | 1. Prepare tool, consumable & spare parts 2. Open the manhole 3. Clean tube of heater with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 3. Check condition of welded joints 4. Tube of heater leak check 5. Prepair/ build-up the welding depends on leak test result. 6. Replace the manhole gasket, partition gasket. 7. Close the manhole 8. Inspection report. | Set | 1 |
| TBN | Feedwater System | 8 | External Desuperheater of Feedwater Heater No.6 (Feedwater Heater No.9) Overhaul | 1. Prepare tool, consumable & spare parts 2. Open the manhole 3. Clean tube of heater with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 3. Check condition of welded joints 4. Tube of heater leak check 5. Prepair/ build-up the welding depends on leak test result. 6. Replace the manhole gasket, partition gasket. 7. Close the manhole 8. Inspection report. | Set | 1 |
| TBN | Feedwater System | 9 | Overhaul For M-BFP Flow Control Valve | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 11. Reassemble the valve 12. Tighten the stud nuts 13. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 14. Inspection report. | Set | 2 |
| TBN | Feedwater System | 10 | Economizer Inlet FCV (LAB70AA081) | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 2 |
| TBN | Condensate System and Condenser | 11 | Condenser #A/B | 1. Prepare tool, consumable, spare part 2. Remove the manhole of the condenser 3. Ventilation and hazardous gas testing inside the condenser 4. Cleaning inside the condenser & visual check welding points connecting 5. Tube Leak inspection 6. Post-cleaning inspection inside the condenser 7. Replace the new gasket 8. Close the manhole 9. Inspection report | Set | 2 |
| TBN | Condensate System and Condenser | 12 | CEP Suction Strainer A/B/C | 1. Prepare disassembly tools 2. Remove the Strainer from the service line 3. Unfasten the screen element and slowly pull the screen outside from the inlet side of the strainer 4. Clean and install the strainer back to service line 5. Inspect flange gasket for cuts or other signs of failure and make sure it is properly seated. 6. Inspection report | Set | 3 |
| TBN | Condensate System and Condenser | 13 | Overhaul for Check Valve on CEP A, B, C Discharge Line | 1. Prepare tools, consumable & spare part 2. Disassembly valve 3. Check leakage from gasket, gland packing & valve seat. 4. NDT inspection 5. Contact check. 6. Replace gasket, gland packing and damaged part if any 7. Reassemble valve. 8. Inspection report | Set | 3 |
| TBN | Condensate System and Condenser | 14 | Overhaul for LP heater #1, 2, 3, 4 | 1. Prepare tool, consumable & spare parts 2. Open the manhole 3. Clean tube of heater with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 3. Check condition of welded joints 4. Tube of heater leak check 5. Prepair/ build-up the welding depends on leak test result. 6. Replace the manhole gasket, partition gasket. 7. Close the manhole 8. Inspection report. | Set | 4 |
| TBN | Condensate System and Condenser | 15 | Condensate Supply To Water Seal Line PCV (P1LCR10AA081) | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 1 |
| TBN | Condensate System and Condenser | 16 | Condensate Supply To Water Seal Line Y-type Strainer | 1. Prepare disassembly tools 2. Remove the Strainer from the service line 3. Unfasten the screen element and slowly pull the screen outside from the inlet side of the strainer 4. Clean and install the strainer back to service line 5. Inspect flange gasket for cuts or other signs of failure and make sure it is properly seated. 6. Inspection report | Set | 1 |
| TBN | Condensate System and Condenser | 17 | Deaerator Inlet Line 100% LCV (P1LCA90AA081) | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 1 |
| TBN | Condensate System and Condenser | 18 | Deaerator Inlet Line 30% LCV (P1LCA90AA082) | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 1 |
| TBN | Condensate System and Condenser | 19 | Condenser Clean-Up Line LCV | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 1 |
| TBN | Condensate Polishing Plant (CPP) | 20 | Prefilter A/B Inlet & Outlet Valves | 1. Prepare tool, consumable, spare part 2. Disconnect and remove the actuator on the valve body. 3. Loosen the lock bolts on the yoke clamp and remove them from valve body 4. Disassemble the valves 5. Clean all gasket surfaces, including the body, and dish, seat, stuffing box and the stem 6. Replace the new seal and packing set 7. Reassemble the valve 8. Mount the actuator on the valve body and connect actuator stem to the valve stem. 9. Inspection report | Set | 8 |
| TBN | Condensate Polishing Plant (CPP) | 21 | Mixed Bed Polisher A/B inlet & Outlet Valves | 1. Prepare tool, consumable, spare part 2. Disconnect and remove the actuator on the valve body. 3. Loosen the lock bolts on the yoke clamp and remove them from valve body 4. Disassemble the valves 5. Clean all gasket surfaces, including the body, and dish, seat, stuffing box and the stem 6. Replace the new seal and packing set 7. Reassemble the valve 8. Mount the actuator on the valve body and connect actuator stem to the valve stem. 9. Inspection report | Set | 8 |
| TBN | Condenser Tube Ball Cleaning System | 22 | Water Box and Condenser Tube Cleaning | 1. Prepare tools/ spare parts/ consumables 2. Check the condition of dirt, bolts, nuts: loose, lost 3. Check the anti-corrosion protection layer of the inner surface 4. Check the condition of the welding and spare parts; Record in the Inspection check list 5. Cleaning the ball trainer; Repair the ball trainer according to the inspection results 6. Close the manhole 7. Inspection report | Set | 4 |
| TBN | Debrisfilter | 23 | Debris Filter #A1, A2, B1, B2 | 1. Prepare tools/ spare parts/ consumables 2. Disconnect inlet and outlet flange of debris filter 3. Disassembly debris filter 4. Clean, Inspection check status of debris filter 5. Repair spare parts damage and replace based on the checking results (if any) 6. Replace the O-ring No.12,15,16,19; Oil seal 13; Flexiseal 14 and disk 18 of Bearing Assembly 7. Assembly debris filter 8. Re-connect inlet and outlet flange of debris filter 9. Touch-up paint for rust points on painting surface 10. Final inspection | Set | 4 |
| TBN | Condenser Air Extraction System | 24 | Condenser Vacuum Pump #A/B/C | 1. Prepare tools/ spare parts/ consumables 2. Remove the pump coupling cover 3. Check coupling alignment and adjust if out of allowable range and adjust if out of allowable range 4. Inspection report | Set | 3 |
| TBN | Condenser Air Extraction System | 25 | Seal Water Cooler #A/B/C | 1. Prepare tool, consumable 2. Drain the remained water inside the cooler 3. Disassembly the cooler 4. Clean the the cooler surface, tubes with with high pressure water & check parts inside the heater (Visual heater surface check & tube wall thickness inspection, etc.) 5. Tube of cooler leak check 6. Repair the channel or tubes were damaged 7. Replace the O-ring of cooler if damaged 8. Check the cover plate front side and rear side 9. Reassemble the cooler 10. Pressure test for cooler 11. Inspection record | Set | 3 |
| TBN | Condenser Air Extraction System | 26 | Basket strainer A/B/C | 1. Prepare disassembly tools 2. Remove the Strainer from the service line 3. Unfasten the screen element and slowly pull the screen outside from the inlet side of the strainer 4. Clean and install the strainer back to service line 5. Inspect flange gasket for cuts or other signs of failure and make sure it is properly seated. 6. Inspection report | Set | 3 |
| TBN | HP PRDS | 27 | HP PRDS steam control valve A/B | 1. Prepare tools, consumable & spare part 2. Dissassembling the gland, Actuator 3. Disassambling the bonnet, 4. Using a lifting device, pull out the valve stem including the jet nozzle and the jet cage from the valve body 5. Disassembing the jet cage, nozzle body and valve stem, inspecting the seating surfaces of the valve stem and valve seat for damage. If necessary, recondition seat and stem by lapping, respectively by grinding 6. Removing the Packing set 5. Check the guide face, sealing face, steam thread of piston bushing, piston ring, Perforated cage trim, Valve stem, Guide bushing, Valve seat, valve body and bonnet 7. Thoroughly clean all parts and check for damage. If any parts are damaged, replace them with stock parts 8. Replace the sealing & packing 9. Assembling the valve 10. Assembling Actuator 11. Inspection report. | Set | 2 |
| TBN | HP PRDS | 28 | LP Bypass steam control valve A/B | 1. Prepare tools, consumable & spare part 2. Disassembling the actuator with yoke from valve 3. Disassembling the gland seal 4. Disassembling the pressure seal bonnet 5. Separating the trim from the valve 6. Clean, inspect, repair or replace any damaged part 7. Replace the sealing & packing 8. Assembly the valve 9. Assembly Actuator 10. Disassemble, inspect and reassemble OP spray nozzles 11. Inspection report. | Set | 2 |
| TBN | HP PRDS | 29 | LP Bypass steam shutoff valve A/B | 1. Prepare tools, consumable & spare part 2. Disassembling the actuator with yoke from valve 3. Disassembling the gland seal 4. Disassembling the pressure seal bonnet 5. Separating the trim from the valve 6. Clean, inspect, repair or replace any damaged part 7. Replace the sealing & packing 8. Assembly the valve 9. Assembly Actuator 10. Inspection report. | Set | 2 |
| TBN | HP PRDS | 30 | LP PRDS water control valve | 1. Prepare tool, consumable 2. Disassembly of the actuator-yoke 3. Remove the bonnet from the body 4. Remove the gasket from the body. If lifting holes are provided on the bonnet spacer or balance cylinder, attach two eye bolts and a sling. Lift the bonnet spacer or balance cylinder from the body. 5. Carefully remove the guide bushing (if supplied) and balance seal from the bonnet spacer making sure the metal parts are not damaged. Remove the eye bolts and sling from the bonnet 6. Place the packing flange and stem clamp around the plug stem. Using the sling by wrapping it under the packing flange, remove the plug/ spindle assembly from the body 7. Remove the packing follower. Remove the packing set using the packing removal tool 8. Remove the packing spacer, taking care not to damage the inside diameter of the bonnet 9. Lift the disk stack or cage assembly from the body. 10. Carefully remove the seat ring from the body, taking care not to damage the seating surface. Remove the seat ring spacer if provided and then remove the flexitallic gasket(s) from the seat ring 11. Clean and inspect all the disassembled parts, repalace damaged parts if necessary. 12. Reassemble the valve with new gasket, seal ring 13. Inspection report. | Set | 2 |
| TBN | HP PRDS | 31 | HP/LP HPU | - Prepare tool, consumable 2. Connect a pressure gauge to the gas filling port to check the gas pressure 3. If the pressure is insufficient, refill with nitrogen gas (N₂) as required. 4. Inspect the gas valve for gas leakage by using the foaming inspection liquid - Replace the filter if necessary 6. Inspection record | Set | 2 |
| TBN | Flash Tank | 32 | Flash Tank A/B | 1. Prepare tool, consumable 2. Open the flashtanks for cleaning and inspection 3. Replace gasket and close the manholes 4. Inspection record | Set | 2 |
| TBN | Circulating Water System | 33 | Circulating Water Pump | 1. Prepare the tools, spare parts, consumables 2. Disconnect motor wiring and main and small piping around the pump. 3. Remove coupling bolts. 3. Remove motor and motor stool 5. Remove pump side coupling hub 6. Lift the pump assembly slowly to vertically by using the lifting lugs and shackles, adjust the chain block for pump weight balancing while lifting pump. Move pump to the maintenance area and positioned it from vertical to horizontal position 7. Remove packing gland, packing, and stuffing box. 8. Remove discharge elbow, drive shaft, shaft coupling, and Retainer rings and then remove Lower column pipe. Verify the match marks on the flange of column pipe and discharge elbow. 9. In the same way remove all column pipe and the respective muff couplings, Retainer rings and shafts. Verify the match marks on the flange of column pipes 10. Remove suction bell mouth from diffuser, and then remove impeller nut, and pull out the impeller. 11. Then remove shaft from diffuser 12. After disassembly, clean all parts and protect the threaded portion of the disassembled shaft by wrapping with tape. Coat machined surfaces with anti-rust agent. 13. Inspect all parts and determine whether repair or replacement is necessary 14. When replacing parts, check thoroughly before assembling 15. When reassembling each part, remove foreign matter in the tapped holes with compressed air and check for defects or dirt on the flange surfaces and mating surfaces. 16. Before reassembly, remove anti-rust agent, check for corrosion and damage 17. Pump assembly 18. Replace consumables (such as O-rings, rubber rings, gland packing, washers, etc.) with new ones. 19. Pump alignment, coupling alignment 20. Inspection report | Set | 1 |
| TBN | Circulating Water System | 34 | Internal Inspection of CW pipe | 1. Prepare tools and materials 2. Manhle open 3. Install and use portable submersible pump for removing seawater 4. Clean, check damage inside piping 5. Repair damage (if any) 6. Final inspection 7. Manhole closed | Set | 1 |
| TBN | TBS Chanels | 35 | TBS Chanels A/B | Cleaning the TBS Chanel A/B - Install the stop logs (Stop gates) - Install and use portable submersible pump for removing seawater - Clean the sand, mud, and debris from the bottom of TBS Channels A/B and check for any damage. Repair if necessary | Set | 2 |
| TBN | Closed Cooling Water System | 36 | Closed Cooling Water Pump #A/B | 1. Prepare tools/ spare parts/ consumables 2. Remove the pump coupling cover 3. Check coupling alignment and adjust if out of allowable range. 4. Inspection report | Set | 2 |
| TBN | Closed Cooling Water System | 37 | Closed Cooling Water Pump #A/B Strainer | 1. Prepare disassembly tools 2. Remove the Strainer from the service line 3. Unfasten the screen element and slowly pull the screen outside from the inlet side of the strainer 4. Clean and install the strainer back to service line 5. Inspect flange gasket for cuts or other signs of failure and make sure it is properly seated. 6. Inspection report | Set | 2 |
| TBN | Closed Cooling Water System | 38 | CCW Heat Exchanger #A /B/C | 1. Prepare disassembly tools 2. Disassemble the plate of Heat exchanger for cleaning and inspection 3. Replace gasket & plates if necessary and reassemble the Heat exchanger 4. Check leakgage 5. Inspection report | Set | 3 |
| TBN | Water Treatment Plant | 39 | SWRO high pressure pump | 1. Prepare tools and Spare parts (Consumables and replacement materials) 2. Remove the pump coupling cover 3. Check the initial parameters and disassemble the pump. 4. Replace the grease, oil 5.Clear and inspection space part and replace if needs 6. Check pump parameters after installation 7. Disassemble, inspection: replace bearings; inspect the impeller, shaft, wearing…; inspect the mechanical seal 8. Inspection report" | Set | 2 |
| TBN | Feedwater Heater System | 40 | Nomal and emergency water flow control valves of Heater No. 8, 7, 6, External. 6, 4, 3, 2, 1A, 1B | 1. Prepare tool, consumable, spare part 2. Supply the instrument air to the actuator for lifting up the 25% position of the valve open to avoid injury or damaging valve parts from disassembly of actuator from bonnet." 3. Loosen the lock bolts on the actuator clamp and remove it from valve stem. 4. Loosen the lock bolts on the yoke clamp and remove them from actuator yoke. 5. Lift up the actuator from bonnet by using slings or chins around the actuator or the lifting eye." 6. Remove the nuts from the bonnet flange studs. 7. Lift the bonnet out of the body. 8. Lift the plug-stem, balance cylinder, cage and seat ring out of the body in sequence. 9. Clean all gasket surfaces, including the body, bonnet, and guide, stuffing box and the steam 10. Visually inspect the valve plug and seat for signs of erosion, pitting, scratched and damage from corrosion. 11. Fit the plug and the seat together. While looking into the bottom of the seat, hold the trim, set against a bright light. If any light can be seen between the plug and seat contact surfaces, this is an indication of poor seat condition. 12. Determine the magnitude of any wear or corrosion damage. Many times the plug and seat contact surfaces can be fully restored by relapping. Replace any parts that cannot be fully restored by relapping. After the restoration of trims, wash plug and seat in solvent to remove all lapping compounds and wipe the parts dry. 13. If the stem has been removed, examine the stem for pitting, scratches, or other damage in the packing box area. If any damage cannot be removed by polishing the stem, replace the stem. 14. Replace the new seat gasket, bonnet gasket, balance seal, back up ring and packing set 15. Reassemble the valve 16. Tighten the stud nuts 17. Mount the actuator on the bonnet and connect actuator stem to the valve stem. 18. Inspection report. | Set | 18 |
| II | Electrical Work Scope |  |  |  |  |  |
| ELE | Boiler Feedwater System | 1 | Boiler feed pump B motor | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | Condensate Water System | 2 | Condensate pump B motor | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | Circulating Water System | 3 | Circulating water pump B motor | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | Air compressor System | 4 | Air compressor A motor | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | Colse Cooling Water System | 5 | Close cooling water pump A motor | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | Water Treatment Plant | 6 | High-Pressure Pump A for SWRO | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - Inspection and cleaning of cooling tubes, fan blowers, and filters, and change silicalgel if required - Check the motor space heater and RTDs. - Motor current transformer testing. - Motor windings and power cable IR testing; motor winding DC resistance testing, tag delta test,... - Oil and grease condition checking; replacement if required. - Motor bearing inspection; measure gap of bearing, thrust bearing, surface., Evaluation condition replacement if required. - Check and maintenance shaft voltage and carbon brush - Align the motor if required -Overall cleaning and touch-up painting if required. | Set | 1 |
| ELE | BLR, ESP, ASH,FGD,WTP | 7 | LV Motor Work | - Prepare tools/ materials/ consumables - Provide the necessary scaffolding if required. - Inspection of foundation and terminals; tightening; bolt torque checking; cleaning; dust blow-out; painting if corrosion is found. - The contractor carries out the entire job from dismantling to reinstalling the motor - Inspection of the cooling fan and filter. - Check the motor space heater and RTDs, if any. - Motor current transformer testing, if any. - Motor windings and power cable IR testing; motor winding DC resistance testing and run tests after installation, - Oil and grease condition checking; replacement if required, Cleaning, and replenishing the grease. - Visual inspection, cleaning rotor, stator, bearing, inner, outer, Motor bearing inspection; replacement if required. - Bolt torque checking. - Align the motor if required. - Overall cleaning and touch-up painting if required. | 84 | EA |

The above service price includes the supervisors, technicians/ equipment & tools, heavy equipment, consumables, … which are needed to complete the job.

The contractor is required to give the break-down unit price for each package with detail in following page.

Man-power rate (which will be applied to pay for any arising job, out of scope in above package)

This will not be included in the total amount of maintenance package.

- To use as an add-off option for any arising work.

- Other costs like (transportation, machining) will be reimbursed based on actual if any.

| No | Category | unit | Unit Price (VND/excl. VAT) |
| --- | --- | --- | --- |
| 1 | Technician/ worker | Man/day |  |
| 2 | Supervisor | Man/day |  |
| 3 | Welder 3G/4G | Man/day |  |
| 4 | Welder 6G | Man/day |  |
| 5 | Scaffolder | Man/day |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |

- Technical Proposal includes

- Maintenance Procedure/ method statement/ ITP

- Safety measures

- Schedule of system

- Manpower mobilization

- Tools, machinery, heavy equipment, and consumable mobilization

- Detail for Boiler 1 pressure tube visual inspection & thickness measurement - Support for Risk Base Maintenance Assessment

| No. | Description | Work scope detail | Quantity | Unit price | Total amount |
| --- | --- | --- | --- | --- | --- |
| 1 | Water wall | Burner & wall blower area: Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 576 |  |  |
|  |  | Cage front wall screen tube: Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 192 |  |  |
| 2 | Platen Superheater | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 512 |  |  |
|  |  | Hardness test (randomly) | 30 |  |  |
|  |  | Replica test (randomly) | 3 |  |  |
| 3 | Final Superheater | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 248 |  |  |
|  |  | Hardness test (randomly) | 30 |  |  |
|  |  | Replica test (randomly) | 3 |  |  |
| 4 | Primary Superheater | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 4940 |  |  |
| 5 | Final Reheater | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 189 |  |  |
|  |  | Hardness test (randomly) | 30 |  |  |
|  |  | Replica test (randomly) | 2 |  |  |
| 6 | Pri. Reheater 1st, 2nd and 3rd horizontal bank | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 13680 |  |  |
| 7 | Economizer | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 2840 |  |  |
| 8 | Slope hopper | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 500 |  |  |
| 9 | Cage side wall & Vestibule side wall | Tube thickness measurement, including Visual inspection & fouling cleaning for measuring points. | 172 |  |  |
|  |  | Replica test (randomly) | 3 |  |  |
| 10 | Vestibule floor | PT for membrane (length 230 meters) | 230 |  |  |
| 11 | Vestibule side wall | PT for membrane (length ~20 meters) | 20 |  |  |
| 12 | Penthouse | PT for membrane (Randomly with length 30 meters (30%)) | 30 |  |  |

- Reference documents

  - Boiler

| No. | Document no. | Description |
| --- | --- | --- |
| 1 | VA2-YD00-P1ZEN-320002 | Boiler General Arrangement |
| 2 | VA2-YD00-P1HA-320030 | Pressure part arrangement- platen SH |
| 3 | VA2-YD00-P1HA-320040 | Pressure part arrangement- final SH |
| 4 | VA2-YD00-P1HA-320070 | Pressure part arrangement- final RH |
| 5 | VA2-YD00-P1HA-320075 | Pressure part arrangement- primary RH |
| 6 | VA2-YD00-P1HA-320050 | Pressure part arrangement- primary SH |
| 7 | VA2-YD00-P1HA-320060 | Pressure part arrangement- economizer |
| 8 | VA2-YD00-P1HA-320085 | Pressure part arrangement- Vestibule side & Cage side wall |
| 9 | VA2-YD00-P1HA-320090 | Pressure part arrangement-Spiral side wall |

  - Turbine

| No. | Document no. | Description |
| --- | --- | --- |
| 1 | VA2-YK08-P1PBB-460202 | DRAWING_HEX_DEBRIS FILTER_Rev.0 |
| 2 | VA2-YK09-P0PAC-120001 | CWP_PUMP SECTIONAL DRAWING |
| 3 | VA2-YK10-P1LAC-120001 | BOILER FEEDWATER PUMP - PUMP SECTIONAL DRAWING_Rev.1 |
| 4 | VA2-YK10-P1LCB-120001 | CONDENSATE EXTRACTION PUMP - PUMP SECTIONAL DRAWING_REV.0 |
| 5 | VA2-YR05-P0ZEN-150001 | Control Valve for BOP - Technical Specification Datasheet_Rev.0 |
| 6 | VA2-YS18-P1MAN-120001 | Bypass System and PRDS_HPU Circuit Diagram for Bypass System IFI 3 |
| 7 | VA2-YK08-P1LAD-430001 | OUTLINE DRAWING FOR HP FEEDWATER HEATER NO.6_REV.1 |
| 8 | VA2-YK08-P1LAD-430002 | OUTLINE DRAWING FOR HP FEEDWATER HEATER NO.7_REV.1 |
| 9 | VA2-YK08-P1LAD-430003 | OUTLINE DRAWING FOR HP FEEDWATER HEATER NO.8_REV.1 |
|  | VA2-YK08-P1LAD-430004 | OUTLINE DRAWING FOR EXTERNAL DESUPERHEATER OF HP FEEDWATER HEATER NO.6_REV.1 |
|  | VA2-YK08-P1LCC-440002 | OUTLINE DRAWING FOR LP FEEDWATER HEATER NO.2_REV.1 |
|  | VA2-YK08-P1LCC-440003 | OUTLINE DRAWING FOR LP FEEDWATER HEATER NO.3_REV.1 |
|  | VA2-YK08-P1LCC-440004 | OUTLINE DRAWING FOR LP FEEDWATER HEATER NO.4_REV.1 |
|  | VA2-YK08-P1LCC-440051 | Outline Drawing For LP Feedwater Heater No.1A,1B |

  - Electrical

| No. | System | Drawing code | Discription |
| --- | --- | --- | --- |
| 39 | MV Motor | VA2-YT01-P1LAC-120012 | Boiler Feed Water Pump Motor |
| 40 |  | VA2-YM01-P1HNC-320036 | C.I.D Fan Motor |
| 41 |  | VA2-YT01-P0PAC-120002 | Circulating Water Pump Motor |
| 42 |  | VA2-YM01-P1HFE-320026 | P.A. Fan Motor |
| 43 |  | VA2-YM01-P1HLB-320016 | F.D. Fan Motor |
| 44 |  | VA2-CV03-P1HFC-320001 | Motor for Pulverizer |
| 45 |  | VA2-YT01-P1LCB-120007 | Condensate Extraction Pump Motor |
| 46 |  | VA2-YT01-P1HAG-320001 | Boiler Recirculation Pump Motor |
| 47 |  | VA2-YT01-P1PGB-120002 | Closed Cooling Water Pump Motor |
| 48 |  | VA2-YT01-P0SCA-120003 | Air Compressor Motor |
| 49 |  | VA2-YT10-P0BCF-530001 | PROTECTION RELAY COORDINATION STUDY OF MV SWITCHGEAR FOR FGD |
| 50 | LV Motor | VA2-YT01-P0GCF-120003 | [water treatment plant]_PUMP & MOTOR DATASHEET |
| 51 |  | VA2-CV03-P1HFC-320003 | Classifier Motor Specification for Pulverizer |
| 52 |  | VA2-YT10-P0BHF-530001 | PROTECTION RELAY COORDINATION STUDY OF LV SWITCHGEAR AND MCC FOR FGD |

Annex 02_ PROPOSAL FORM

PHỤ LỤC 02_ BIỂU MẪU BẢN CHÀO GIÁ

(Company letterhead/Tiêu đề công ty)

Date/ Ngày tháng:

To: VUNG ANG II THERMAL POWER LLC (VAPCO)

Kính gửi: CÔNG TY TNHH NHIỆT ĐIỆN VŨNG ÁNG II (VAPCO)

Attn: Mr. Pham Ngoc Thach, Procurement & Contract Leader

Attn: Mr. Ha Jong Woo– GA & Contract Manager

We, _____(your company name)_______, undersigned, hereby offer to supply Unit 1 overhaul services- Electrical to Vung Ang II Thermal Power LLC in compliance with VAPCO’s RFP #VAPCO/PS-50182-1 dated 15 April 2026.

Chúng tôi, ____(tên đơn vị)________, ký tên dưới đây, chào giá cung cấp các dịch vụ tiểu tu Tổ máy 1-  Điện cho Công ty TNHH Nhiệt điện Vũng Áng II tuân thủ Yêu cầu chào giá của VAPCO số VAPCO/PS-50182-1 ngày 15/04/2026.

| No. Số | Item* Hạng mục | Unit and Quantity Đơn vị và Số lượng | Completion time Thời gian hoàn thành | Unit price Đơn giá (VND) | Total price Thành tiền (VND) |
| --- | --- | --- | --- | --- | --- |
| I |  |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| … |  |  |  |  |  |
| Total Price (excluding VAT)/ Tổng Giá trị (chưa bao gồm VAT) |  |  |  |  |  |

* Bidders to quote the corresponding items covered under each item of the Scope of Service

- Terms and conditions/ Các điều khoản và điều kiện:

The price is exclusive VAT but inclusive of all applicable taxes, duties or other applicable expenses

Giá chưa bao gồm thuế GTGT nhưng đã bao gồm các loại thuế, phí và các chi phí liên quan khác.

Total payment will be made within 30 days of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Contact Person/ Đầu mối liên hệ:

Contact person	:			Position

Đầu mối liên hệ: 			Chức danh

Telephone	: 			Email:

Số điện thoại: 				Email:

|  | Legal representative of Bidder Người đại diện pháp lý của Nhà thầu [Full name, position, signature and seal [Họ tên, chức vụ, chữ ký và con dấu] |
| --- | --- |

Annex 03_ CONTRACT FORM

PHỤ LỤC 03_ MẪU HỢP ĐỒNG

(from the next page/ từ trang sau)