[ATTACHMENT 1]

REQUEST FOR PROPOSAL

THƯ MỜI CHÀO GIÁ

Ref: VAPCO/PS-50182-3

To: Potential Bidders

Copy to:

Subject: Supply of Unit 1 minor overhaul services- Instrument and Controls/ Cung cấp các dịch vụ tiểu tu Tổ máy 1- Thiết bị đo lường và Điều khiển

- Date: 15 April 2026/ Ngày 15/04/2026

- InstructionS to the participating bidders

Chỉ dẫn đối với các nhà thầu tham gia

  - General information

Thông tin chung

Vung Ang II Thermal Power LLC (VAPCO), the Owner of 2 x 600MW ultra super-critical imported coal-fired thermal Power Plant in Vung Ang Ward, Ha Tinh Province, Vietnam that is being undertaken on a build-operate-transfer basis under Vietnam law, issuing this Request for Proposal (RFP) to invite bidders, who are interested in contracting with VAPCO for the supply of Unit 1 minor overhaul services as detailed in Annex 01.

Công ty TNHH Nhiệt điện Vũng Áng II (VAPCO), Chủ đầu tư Nhà máy Nhiệt điện đốt than nhập khẩu trên siêu tới hạn với công suất 2 x 600MW tại phường Vũng Áng, tỉnh Hà Tĩnh, Việt Nam đang thực hiện dự án xây dựng-kinh doanh-chuyển giao theo pháp luật Việt Nam, ban hành Thư mời chào giá (RFP) này để mời các Nhà thầu quan tâm đến việc ký hợp đồng với VAPCO để cung cấp dịch vụ tiểu tu Tổ máy 1 với mô tả chi tiết như ở Phụ Lục 01.

The service is expected to commence in November 2026.

Dịch vụ dự kiến được bắt đầu trong tháng 11 năm 2026.

  - Compliance with RFP requirements

Tuân thủ các yêu cầu của Thư mời chào giá

The participating bidders shall prepare and submit a Proposal in compliance with the procedures and requirements as outlined in this RFP.  Any omission may give VAPCO a reason to reject or unfavorable evaluation of the Proposal. The participating bidders will be deemed to have fully understood and accepted all the contents of the RFP. Upon submission of a Proposal, the bidders are deemed to have agreed to fully comply with the Contract’s General Terms and Conditions as attached to the RFP.

Các bên tham gia sẽ chuẩn bị và nộp Bản chào tuân thủ các quy trình và yêu cầu như được quy định trong Thư mời chào giá này. Bất kỳ sự sai sót nào có thể khiến VAPCO có lý do từ chối hoặc đánh giá bất lợi cho báo giá. Các bên tham gia sẽ được coi là đã hiểu hoàn toàn và chấp nhận tất cả các nội dung trong Thư mời chào giá. Sau khi nộp Bản chào, khi đó thầu được coi là đã đồng ý tuân thủ đầy đủ các Điều khoản và Điều kiện chính của Hợp đồng như được đính kèm trong Thư mời chào giá.

  - Confidentiality

Bảo mật

The prices in the Proposal must be issued independently, and not be consulted, communicated, or negotiated with any other bidders.

Các giá trong Bản chào của nhà thầu phải được chào độc lập, không được tham khảo, liên lạc hoặc thỏa thuận với bất kỳ nhà thầu nào khác;

The prices stated in the Proposal have not been intentionally disclosed by the bidder and will not be knowingly disclosed, directly or indirectly, to any other participant before the Proposal submission deadline. Furthermore, these prices have not been used, and will not be used, to influence or induce any other person or company to submit, refrain from submitting, or otherwise restrict competition in any way

Các mức giá nêu trong Bản chào chưa từng được nhà thầu cố ý tiết lộ và sẽ không được tiết lộ có chủ đích, trực tiếp hoặc gián tiếp, cho bất kỳ bên tham gia nào khác trước thời hạn nộp Bản chào. Hơn nữa, các mức giá này chưa từng và sẽ không được sử dụng để tác động hoặc lôi kéo bất kỳ cá nhân hay công ty nào nộp, không nộp hồ sơ hoặc hạn chế cạnh tranh dưới bất kỳ hình thức nào.

Participating bidders must not disclose the RFP to any third parties who are not directly involved in the preparation of the Proposal.

Những người tham gia không được tiết lộ Thư mời chào giá cho bất kỳ bên thứ ba nào không liên quan trực tiếp đến việc làm báo giá.

  - Withdrawal of procurement

Thu hồi yêu cầu mua sắm

VAPCO reserves the right, at any time and without any liability to the participants, to cancel, delay or extend this procedure or to change the scope of the procurement.

VAPCO có quyền, bất cứ lúc nào và không có bất kỳ trách nhiệm nào đối với các bên tham gia, trong việc hủy bỏ, trì hoãn hoặc gia hạn thủ tục này hoặc thay đổi phạm vi mua sắm.

  - Language

Ngôn ngữ

The documents shall be prepared in English and Vietnamese. If there is any difference or inconsistency between English and Vietnamese, the English language shall prevail.

Các tài liệu được chuẩn bị bằng tiếng Anh và tiếng Việt. Nếu có bất kỳ sự khác biệt hoặc mâu thuẫn nào giữa tiếng Anh và tiếng Việt thì bản tiếng Anh sẽ được áp dụng.

  - Currency and Payment

Tiền tệ và thanh toán

The price shall be quoted in Vietnamese Dong, exclusive of VAT.

Giá được chào giá bằng đồng Việt Nam, chưa bao gồm thuế GTGT

Payment shall be made in Vietnamese Dong.

Thanh toán được thực hiện bằng đồng Việt Nam.

- Procedures for RFP

Thủ tục mời chào giá

  - Clarification of bidding information

Làm rõ thông tin mời thầu

The participating bidders are requested to study and carefully check the contents of the bidding information and other relevant information. The bidders may send an email to VAPCO’s PIC: Mr. Pham Ngoc Thach, at thach.pham@vapco.com.vn (copying: Mr. Ha Jong Woo, at jeff.ha@vapco.com.vn) or an official letter to VAPCO regarding the unclear contents at least 5 days before the due date of letter of Proposal submission. Written clarifications or feedback via email (as the case may be) will be provided by VAPCO no later than 1 day before the due date of Proposal submission.

Nhà thầu tham gia được yêu cầu nghiên cứu và kiểm tra kỹ lưỡng nội dung của thông tin mời thầu và các thông tin liên quan khác. Các Nhà thầu có thể gửi email cho VAPCO: Ông Phạm Ngọc Thạch theo địa chỉ thach.pham@vapco.com.vn (cc cho ông Ha Jong Woo tại jeff.ha@vapco.com.vn) hoặc thư chính thức đến VAPCO về các nội dung không rõ ít nhất 5 ngày trước ngày hết hạn nộp Hồ sơ chào giá. Giải thích bằng văn bản hoặc phản hồi bằng email (tuỳ trường hợp cụ thể) sẽ được VAPCO cung cấp không muộn hơn 1 ngày hết hạn nộp bản chào.

At any time, before 3 days before the due date of Proposal submission, VAPCO has the right to amend or add to the bidding information. The amendment or supplement shall be communicated in writing to all participating bidders and the bidders shall be obliged to comply with such addition or amendment.

Vào bất kỳ thời điểm nào trước khi hết hạn nộp hồ sơ chào giá 3 ngày. VAPCO có quyền sửa đổi, bổ sung thông tin mời thầu. Việc sửa đổi, bổ sung sẽ được thông báo bằng văn bản tới tất cả các nhà thầu tham gia và các nhà thầu có nghĩa vụ tuân thủ việc bổ sung, sửa đổi đó.

  - Submission of Proposal

Nộp Bản chào

Each bidder will finalize and fill out the form given in Item 4.

Mỗi nhà thầu tham gia sẽ hoàn thiện và điền vào biểu mẫu tại Mục 4.

Bidders are required to submit supporting documents for Technical Evaluation as follows:

- Certificate of business registration

- Reference contracts and completion certificates to supply overhaul services to thermal power plants for the last 7 years

- Work Method Statement inluding detailed overhaul execution plan and heavy equipment and tools deployment plan

- Quality assurance and control plan and procedures

- Risk Assessment Report for technical risk identification and mitigation

- CV of the Project Manager and key engineers showing qualification and overhaul experience

- Detailed schedule at Primavera/ MS Project Level

- Delay Recovery Plan with acceleration strategy

- HSSE Policy, Plan and Procedures

- Safety record showing LTIR/TRIR for the last 3 years

Các nhà thầu phải nộp các giấy tờ chứng minh cho mục đích Đánh giá kỹ thuật như sau:

- Giấy đăng ký kinh doanh của nhà thầu

- Các hợp đồng và chứng nhận hoàn thành tham chiếu cho việc cung cấp dịch vụ kỹ thuật bảo trì cho nhà máy nhiệt điện trong vòng 7 năm qua

- Thuyết minh biện pháp thi công bao gồm kế hoạch triển khai công việc và kế hoạch huy động phương tiện, thiết bị và dụng cụ

- Kế hoạch và quy trình kiểm soát và đảm bảo chất lượng

- Báo cáo đánh giá rủi ro nhằm nhận diện và hạn chế các rủi ro kỹ thuật

- CV của Quản lý dự án và các kỹ sư chính nêu rõ bằng cấp và kinh nghiệm trong tiểu tu

- Bảng tiến độ công việc chi tiết trên nền tảng Primavera/ MS Project Level

- Kế hoạch phục hồi sau gián đoạn với chiến lược tăng tốc

- Chính sách, Kế hoạch và Các quy trình HSSE

- Hồ sơ an toàn bao gồm các thông tin về LTIR/TRIR trong 3 năm qua

Bidders are required to attach a Letter of Confirmation that by submitting the Proposal, they have understood and accepted all major terms and conditions of Part III- Key Terms and Conditions, Annex 01- Scope of Service, and Annex 03- Contract Form of this RFP.

Các nhà thầu phải đính kèm Thư xác nhận rằng bằng việc nộp Thư chào giá, họ đã hiểu và chấp nhận các điều kiện và điều khoản chính của Phần III- Điều kiện và Điều khoản chính, Phụ lục 01- Phạm vi Dịch vụ và Phụ lục 03- Mẫu hợp đồng.

The Proposal Form and other documents shall be submitted by email to the following address no later than the deadline to:

Bản chào sẽ được gửi bằng email đến địa chỉ sau không muộn hơn thời hạn:

Mr. Pham Ngoc Thach / Procurement & Contract Leader,

Vung Ang II Thermal Power LLC,

Address : Vung Ang Economic Zone, Vung Ang Ward, Ha Tinh,

Email: thach.pham@vapco.com.vn,  Phone No: 0986040681,

Copying: Mr. Ha Jong Woo, GA & Contract Manager,

Email: jeff.ha@vapco.com.vn

The Proposal Form will be encrypted to ensure that it won’t be opened before the time specified in Item 3 below.

Bản chào giá sẽ được mã hóa nhằm đảm bảo không được mở trước thời gian quy định trong Điều 3 sau đây.

Email subject: The bidders are kindly requested to clearly state the bidding package’s name and the bidder's name (e.g.: "Proposal for supply of Unit 1 minor overhaul services / "Bidder's name").

Tiêu đề thư: Nhà thầu ghi rõ tên gói thầu và tên nhà thầu (ví dụ: “Bản chào cho việc cung cấp dịch vụ tiểu tu Tổ máy 1 / "Tên nhà thầu”).

(The bidder may contact Mr. Pham Ngoc Thach for confirmation of the sent email/Nhà thầu có thể liên hệ với Ông Phạm Ngọc Thạch để xác nhận email đã gửi thành công).

  - Deadline for submission of the Proposal

Thời hạn nộp bản chào giá:

The due date for Proposal submission is 17:00, 07 May 2026

Ngày hết hạn nộp bản chào giá: 17:00, ngày 07/05/2026

The bidder will share the password to open the pdf file of the Proposal Form via email by 09:00, 08 May 2026.

Nhà thầu sẽ gửi mật khẩu để mở Bản chào giá qua email vào 9:00 ngày 08/05/2026.

  - Validity period

Thời hạn hiệu lực

The Proposal shall be offered and valid for 120 days from the due date of Proposal document submission. VAPCO may request to extend the validity time of the Proposal and notify it in writing. The extension time shall not exceed 15 days. If the bidder fails to accept the extension of the validity time, its Proposal will not be considered for evaluation.

Chào giá được đưa ra và có hiệu lực trong vòng 120 ngày kể từ ngày hết hạn nộp hồ sơ chào giá. VAPCO có thể yêu cầu gia hạn thời gian hiệu lực của chào giá và thông báo bằng văn bản, thời gian gia hạn sẽ không vượt quá 15 ngày. Trường hợp nhà thầu tham gia không chấp nhận gia hạn thời gian hiệu lực thì chào giá đó sẽ không được xem xét để đánh giá.

  - Bid evaluation and award criteria

Tiêu chí đánh giá hồ sơ dự thầu và lựa chọn

Proposal evaluation

Đánh giá Bản chào

The bidders' Proposal will be considered and evaluated when they fully meet the above criteria, and the document is submitted as prescribed in Item 2.2 before the deadline or subject to VAPCO’s decision.

Bản chào của Nhà thầu chỉ được xem xét đánh giá khi đáp ứng đầy đủ các tiêu chí nêu trên và nộp bộ hồ sơ như quy định tại Mục 2.2 trước thời điểm đóng thầu hoặc theo quyết định của VAPCO.

- Technical evaluation

Đánh giá về kỹ thuật

- Financial evaluation:

Đánh giá về tài chính

The bidder with the highest combined score from both technical and financial evaluations will be selected as the preferred bidder and invited to enter the contract negotiation stage.

Nhà thầu nào đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính sẽ được chọn vào giai đoạn thương thảo hợp đồng.

- Award Criteria

Tiêu chí lựa chọn

VAPCO will award the Contract to the bidder with the highest combined score from both technical and financial evaluations and favourable terms after negotiation.

VAPCO sẽ ký hợp đồng với Nhà thầu đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính và các điều khoản phù hợp nhất sau khi đàm phán.

VAPCO has the right to adjust the Scope of Service at its discretion.

VAPCO có thể điều chỉnh Phạm vi Dịch vụ theo quyền quyết định của mình.

  - Announcement of evaluation result

Thông báo kết quả đánh giá

The evaluation result might be announced to all participants after the decision on approval of the result. In the notice of the evaluation result, VAPCO is not obligated to explain the reasons for the unsuccessful bidders.

Kết quả đánh giá có thể được thông báo cho các bên tham gia sau khi có quyết định phê duyệt kết quả đánh giá cuối cùng. Trong thông báo kết quả đánh giá, VAPCO không có nghĩa vụ giải thích lý do đối với các nhà thầu không được lựa chọn.

  - VAPCO’s option

Tùy chọn của VAPCO

VAPCO reserves the right, without any liability to the parties, to modify or withdraw this RFP at any time, to increase or decrease the Scope of Service included in the Contract or request to restart the procedure when deemed valid is of the greatest interest to VAPCO and rejects any or all the Proposals. No claim regarding any modification, withdrawal, or restart of the process will be accepted by VAPCO. VAPCO also has the option to award the Contract to an acceptable participant, whichever is in the best interest of the company.

VAPCO bảo lưu quyền, mà không có bất kỳ trách nhiệm nào đối với các bên tham gia, sửa đổi hoặc rút lại Yêu cầu chào giá này bất cứ lúc nào, để tăng hoặc giảm phạm vi công việc được đưa vào Hợp đồng hoặc yêu cầu khởi động lại thủ tục khi được coi là hợp lệ được VAPCO quan tâm nhất và từ chối bất kỳ hoặc tất cả các đề xuất. Không có yêu cầu bồi thường liên quan đến bất kỳ sửa đổi, rút lui hoặc khởi động lại quá trình sẽ được VAPCO chấp nhận. VAPCO cũng có tùy chọn để trao hợp đồng cho bên tham gia chấp nhận được, tùy theo điều kiện nào là tốt nhất cho lợi ích của công ty.

  - Compliance in bidding

Tuân thủ trong đấu thầu

The bidders must comply with the provisions of the law on anti-corruption, anti-bribery, and anti-monopoly and commit to bidding standards to ensure healthy competition, fairness, and transparency.

Các nhà thầu phải tuân thủ các quy định của pháp luật về phòng chống tham nhũng, chống hối lộ, chống độc quyền và cam kết các tiêu chuẩn đấu thầu đảm bảo cạnh tranh lành mạnh, công bằng và minh bạch.

- Key terms and conditions

Điều khoản và điều kiện chính

  - Contract term

Thời hạn Hợp đồng

The Contract shall come into effect upon signing and shall remain in force until both parties have fulfilled their contractual obligations.

Hợp đồng sẽ có hiệu lực kể từ ngày ký và sẽ có hiệu lực cho đến khi hai bên hoàn thành nghĩa vụ theo hợp đồng

  - Contract price

Giá trị Hợp đồng

The Contract price is based on a fixed-unit price.

Giá trị Hợp đồng được tính trên cơ sở đơn giá cố định.

  - Payment

Thanh toán

Total payment will be made within 30 days from the date of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Proposal form

Mẫu bản chào giá

Bidders are encouraged to submit their Proposals using the following form as per Annex 02.

Nhà thầu được khuyến nghị nộp bản chào theo mẫu ở Phụ Lục 02 sau đây.

Annex 01_ SCOPE OF SERVICE/

PHỤ LỤC 01_ phạm vi DỊCH VỤ

- Scope of overhaul maintenance services for Lot 3 (Instrument and Controls)

| Dept | Item | Unit | System/area | Description | Unit | Quantity | Equipment qtty | Scope of Work |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| IC | 1 | U1 | TCS | System health check, backup program, Panel filter cleaning, replace fan, filter, clean the TCS computer. | Package | 1 | 7 | System health check: 1.1 Check hardware status including CPU, IO Module, network module inside cabinet and on software Tosmap. 1.2 Back up progam including logic database and HMI graphic. 1.3 Clean and dust suction for 04 computers. |
|  |  |  |  | Remove Instruments of Turbine bearing (support for a Turbine mechanical team to inspect bearing) |  |  | 64 | 1.1 Measure and record the gap, voltage for vibration sensors, thrust position, before dismantling them. 1.2 Dismantle the vibration sensors ( total 16 sensors) 1.3 Inspect and evaluate the vibration sensor, replace the sensors that do not meet the requirement. 1.4 Dismantle and inspect the status for temperature sensor. |
|  |  |  |  | Re-install Instruments of Turbine |  |  | 64 | Install all vibration and temperature sensors, and check the values on the TCS. Ensure that the gap and voltage are the same as the previous readings |
| IC | 2 | U1 | DCS | System health check, Panel filter cleaning, tightening (Cabinet) | Package | 1 | 50 | 1. Check items in panel. 2. Clean dust in DCS use vacuum machine. 3. Tighten all cable terminal 4. Clean PC in OWS by vacumm machine. |
| IC | 3 | U1 | DCS | Failover test ( Controller, LAN Switch, Power) | Package | 1 | 1 | 1. Controller fail over test. 2. Power fail over test. 3. Lan switch fail over test. 4. Scada, OPC fail over test. |
| IC | 4 | U1 | DCS | Back up program, graphic, database. ELC review communication statistics for loading and errors. | Package | 1 | 1 | 1. Back up logic diagram. 2. Back up graphic diagram. 3. Back up database ( Partial back up). 4. Full system back up. 5. ELC review communication statistíc for loading errors. |
| IC | 5 | U1 | PLC | All PLC system: FGD, ASH, ESP, INTAKE, ECP, CPP, Air Compressor inspection, health check, PM and backup program | Package | 1 | Common : 19 Unit #1 : 11 | 1. Check items in panel 2. Clean dust in PLC use vacuum machine 3. Tighten all cable terminal 4. Clean PC in OWS by vacumm machine 5. Back up logic and HMI to CD |
|  |  |  |  | PLC system valve stroke test and setting feeback |  | 1 | 300 | 1. Check valve site condition 2. Operate valve from HMI 3. Check feedback to HMI 4. Setting limit switch |
| IC | 6 | U1 | VMS | System health check, Panel filter cleaning, check vibration sensor. | Package | 1 | 5 | 1. Check items in panel. 2. Clean dust in VMS use vacuum machine. 3. Tighten all cable terminal 4. Check vibration sensor gap and re-setting. 5. Tighten the vibration terminal and sensor. |
| IC | 7 | U1 | Turbine | Turbine auxilary system: HPU, lube oil, seal oil, stator cooling system PM job: cleaning and tightening JB, calibrate for pressure switches. | Package | 1 | 10 | 1.1 Tighten the JB, connection points at sensors, transmitters, switches. 1.2 Testing and calibrate for the pressure switches if deviation. |
| IC | 8 | U1 | Turbine | HP/LP heater levels& condensate level calibration | Package | 1 | 20 | 1.1 Clean the impulse piping and fill out water inside. 1.2 Check zero and span for transmitters. 1.3 Check the leak and tighten the connection point of piping. |
| IC | 9 | U1 | Turbine | Turbine Trip signal test | Package | 1 | 48 | 1.1 Use HART to simulate the trip value at instrument to check alarm, trip on TCS ( 24 signals) |
| IC | 10 | U1 | Turbine | Testing, tightening feedback connection points and recalibration for critial pneumatic control valves in a Turbine area (attached list) | Package | 1 | 45 | 1.1 Test valves and measure the stroke, respond time according to datasheet, detect any sticking and repair it. 1.2 Check the air leak at booster, positioner and tighten the terminal inside the positioner, feedback rod and JB. |
| IC | 11 | U1 | Turbine | Generator H2 and CO2 system Inspection, instrument health check | Package | 1 | 10 | 1.1 Check status of controller, H2 measurement rank 1.2 Repair if any abnormalities occurs. 1.3 Check and calibrate level transmitter; KOH flow switch, HTO, |
| IC | 12 | U1 | Turbine | Turbine CV (MSV, RV, ICV, CV) stroke test, and calibration if needed and confirmed by manager. | Package | 1 | 8 | 1. Visual Inspection for 8 steam contol valves 2. Remove wiring, cable of valves instrument if the turbine mechanical tem needs to inspect valves. 3. Reinstall wiring, cable of valves instrument 4. Caliration, stroke test. |
|  |  |  |  | Remove wiring, cable of valves instrument if the turbine mechanical tem needs to inspect valves |  |  |  |  |
|  |  |  |  | Reinstall wiring, cable of valves instrument |  |  |  |  |
| IC | 13 | U1 | BFP | - Check and tighten all trip signals for BFPs including vibrations, speed, overspeed and temperature ( gap, voltage..) | Package | 1 | 140 | 1.1 Measure and record the gap, voltage for vibration sensors,speed. 1.2 Check and stroke test for scoop tube for BFPs. 1.3 Test the pressure transmitters and switches, and calibrate them if there is any deviation. 1.4 Check the right position X,Y for vibrations and temperature displayed on DCS. 1.5 Fill out the water in to the impulse piping for DP transmitter. |
|  |  |  |  | - Check and stroke test for scoop tube for BFPs. |  |  |  |  |
|  |  |  |  | - Test the pressure transmitters and re calibration if needed. |  |  |  |  |
| IC | 14 | U1 | CEP | - Check and tighten all trip signals for CEPs (vibration, temperature) | Package | 1 | 40 | 1.1 Measure and record the gap, voltage for vibration sensors. 1.2 Tighten all JB, connection points at sensor. 1.3 Check the value on DCS and fix any abnomalities. |
| IC | 15 | U1 | HP/LP bypass | -Test and calibration Pressure transmitters if needed | Package | 1 | 12 | 1.1 Back up program at local controller. 1.2 Stroke test and calibration for CVs, TCVs if needed, coordinate with a mechanical team to fix any sticking issues. 1.3 Tighten all terminals in local controller cabinet and connection points at sensors, transmitters. |
|  |  |  |  | - Back up program at local controller. |  |  |  |  |
|  |  |  |  | - Stroke test and calibration for CVs, TCVs if needed, coordinate with a mechanical team to fix any sticking issues. |  |  |  |  |
| IC | 16 | U1 | CWP | - Tighten all trip signals including vibrations, temperature, level | Package | 1 | 32 | 1.1 Inspect the TBS levels, tighten all trip signals at sensor and JB. 1.2 Adress the existing abnomaltities |
| IC | 17 | U1 | Boiler | Cleaning and function test for flame scaner | Package | 1 | 48 | 1. Cleaning and function test for flame scaner 2. Tighten all flarme scanner signal. |
| IC | 18 | U1 | Boiler | Boiler MFT signal test | Package | 1 | 210 AI 36 DI | 1. Simulation for test MFT push button. 2. Simulator temperature, pressure transmiter for test MFT. 3. Simulator main equipment related to MFT for test ( BFP,FDF,CIDF ..) |
| IC | 19 | U1 | Boiler | Coal feeder A to F Inspection and calibration (Full scale calibration). | Package | 1 | 6 | 1. Coal feeder A to F Inspection and calibration (Full scale calibration). 2. Tight all signal in Coal Feeder cabinet. |
| IC | 20 | U1 | Boiler | SA, PA control damper, shutoff damper inspection & PM | Package | 1 | 36 | 1. Check the air leak at booster, positioner and tighten the terminal inside the positioner, feedback rod and JB.. 2. Re-calibration damper. |
| IC | 21 | U1 | Boiler | Pulverizer, roller & vent cycle valve's limit SW PM | Package | 1 | 30 | 1. Pressure transmiter purge. 2. All valve strock test and signal to DCS check limit switch signal then adjust limit switch. 3. Hydraulic system leak check and function operater test. 4. Tighten signal in pulverizer cabinet. |
| IC | 22 | U1 | Boiler | Performance supervisory transmitter, sensor inspection & verification (Critical instrument) | Package | 1 | 616 | 1. Pressure transmiter tighten and calibration. 2. temperature transmiter checking condition on HMI and calibration if the signal wrong. |
| IC | 23 | U1 | Boiler | Economizer Hydraulic dampers inspection and calibration | Package | 1 | 5 | 1. Strock test damper and calibtaion. 2. hydraulic system check leak and valve condition check. 3. tighen signal in control cabinet. |
| IC | 24 | U1 | Boiler | Draft Fan (ID, FD, PA Fan) checking strock test for Fan Blade and calibration if necessary. | Package | 1 | 6 | 1. Hydraulic system leak check and tighten. 2. Strock test and coordinate with boiler cheking , calibration if deviation. |
| IC | 25 | U1 | Boiler | BTLD System health check and inspection | Package | 1 | 1 | 1. Check items in panel. 2. Clean dust in BTLD use vacuum machine. 3. Tighten all cable terminal |
| IC | 26 | U1 | FGD | FGD inlet, outlet, emergency dampers PM | Package | 1 | 3 | 1. Limit Switch checking and adjust. 2. Instrument air control checking leak and tignten. 3. Strock test damper for checking actual condition. |
| IC | 27 | U1 | FGD | FGD Absorber pressure, flow, level transmitters PM | Package | 1 | 26 | 1. Checking condition on HMI . 2. tighten signal and calibration if nescessary. |
| IC | 28 | U1 | FGD | FGD CV's stroke check and recalibration as needed | Package | 1 | 64 | FGD CV's stroke check and recalibration as needed |
| IC | 29 | U1 | ESP | ESP hopper, economizer & air preheater level switch inspection, replacement as needed | Package | 1 |  | 1. Remove all level switch 2. Visual check and clean 3. Install then test signal to HMI |
| IC | 30 | U1 | Cleaning LCP, JB | Clean, tightening for all LCPs, Junction Boxes | Package | 1 |  |  |
| IC | 31 | U1 | Analyzer | CEMS. SWAS, FGD, ESP, CPP Analyzer's health check, calibration and PM | Package | 1 |  | 1.Visual check analyzer condition 2. Perform cleaning sensor, purging sample probe, sample line. 3. Perform replace dust filter fo gas analyzer. 4. Perform replace pH, conductivity, TSS, DO if senssor damaged. 5. Perform calibration for sensor, analyzer. 6. Cornfirm the reading value on HMI |
| IC | 32 | U1 | Boiler | PM & inspection for O2 analyzer at boiler area | Package | 1 | 6 | 1.Visual check analyzer condition 2. Perform cleaning sensor, purging sample probe, sample line. 3. Perform replace dust filter fo gas analyzer. 4. Perform calibration for sensor, analyzer. 5. Cornfirm the reading value on HMI |
| IC | 33 | U1 | CWP | Re-location the I&C equipments | Package | 1 |  |  |

The above service price includes the supervisors, technicians/ equipment & tools, heavy equipment, consumables, … which are needed to complete the job.

The contractor is required to give the break-down unit price for each package with detail in following page.

- Man-power rate (which will be applied to pay for any arising job, out of scope in above package)

This will not be included in the total amount of maintenance package.

- To use as an add-off option for any arising work.

- Other costs like (transportation, machining) will be reimbursed based on actual if any.

| No | Category | unit | Unit Price (VND/excl. VAT) |
| --- | --- | --- | --- |
| 1 | Technician/ worker | Man/day |  |
| 2 | Supervisor | Man/day |  |
| 3 | Welder 3G/4G | Man/day |  |
| 4 | Welder 6G | Man/day |  |
| 5 | Scaffolder | Man/day |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |

- Technical Proposal includes

- Maintenance Procedure/ method statement/ ITP

- Safety measures

- Schedule of system

- Manpower mobilization

- Tools, machinery, heavy equipment, and consumable mobilization

- Reference documents

| No. | Document No. | Description |
| --- | --- | --- |
| 1 | VA2-XG07-P1MA-210011 | STG - FLOW DIAGRAM OF TURBINE SUPERVISORY INSTRUMENTS SYSTEM_Rev.0 |
| 2 | VA2-YD00-P0CWA-151137 | DCS - Outline & Detail Drawing for System and Marshalling Cabinet |
| 3 | VA2-QM03-P0ZEN-040010 VA2-YK08-P0CRV-151134 VA2-YR05-P0ZEN-151401 | Shop Inspection and Test Procedure for DCS DCS - LAN Configuration Diagram DCS - Outline & Detail Drawing for Power Distribution Cabinet |
| 4 | VA2-CT00-P0CRN-150001 | O&M MANUAL_DCS |
| 5 | VA2-YD00-P0SHA-120004A VA2-YD00-P0SCA-120003 VA2-XW01-P0QH-120003 VA2-CV03-P1QHQ-520012 VA2-YT02-P0HSP-510003 VA2-YD00-P0PUS-120001 VA2-YK08-P1PAH-460105 VA2-YD00-P0GCF-120001 VA2-YD00-P0GN-120001 | PLC LOCAL PANEL DRAWING INTAKE AIR COMPRESSOR - PLC GENERAL ARRANGEMENT DRAWING AUX. BOILER - BOILER CONTROL PANEL WITH PLC SYSTEM SPECIFICATION OUTLINE DRAWING AND SCHEMATIC DRAWING OF PLC FOR ESP TECHNICAL SPECIFICATION OF PLC FOR ASH HANDLING SYSTEM & PYRITE REMOVE SYSTEM CONTROL PANEL ARRANGEMENT DRAWING ECP CONTROL PANEL ARRANGEMENT DRAWING ECP CONTROL PANEL ARRANGEMENT DRAWING WTP CONTROL PANEL ARRANGEMENT DRAWING WWTP |
| 6 | VA2-YR05-P0ZEN-150311 | VMS Technical Specification & Datasheet_Rev.1_AB1 |
| 7 | VA2-XG07-P1MA-210001 VA2-XG07-P1MA-210003 VA2-XG07-P1MA-210005 VA2-XG07-P1MA-210009 | STG - FLOW DIAGRAM OF MAIN AND EXTRACTION STEAM SYSTEM_Rev.3_AB1 STG - FLOW DIAGRAM OF STG LUBE OIL SYSTEM_Rev.3_AB0 STG-FLOW DIAGRAM OF EHC CONTROL OIL SYSTEM STG - FLOW DIAGRAM OF GLAND SEAL STEAM SYSTEM_Rev.4_AB0 |
| 8 | VA2-XG02-P1LCH-110001 | P&ID FOR FEEDWATER HEATER DRAIN AND VENT SYSTEM |
| 9 | VA2-YL01-P1MA-240002 | STG - Hardwired IO List for ST and Aux_Rev.3_AB1 |
| 10 | VA2-CT00-P0ZEN-150002 | OM Manual_BOP_Control Valve |
| 11 | VA2-XG02-P0QJ-120001 | H2 PLANT-P&ID FOR H2 PLANT_Rev.4_AB0 |
| 12 | 05-08_EKT500290 | Instruction and Maintenance Manual Servo actuator for Steam Control Reva |
| 13 | VA2-YK00-P1LAC-120001 | BOILER FEEDWATER PUMP - INSTRUMENT INSTALLATION DETAIL DRAWING_REV.0 |
| 14 | VA2-XG02-P1LCB-120001 | CONDENSATE EXTRACTION PUMP P&ID |
| 15 | VA2-XS01-P1MAN-120001 | BYPASS SYSTEM AND PRDS_OPERATING DESCRIPTION FOR HPU SYSTEM FOR BYPASS SYSTEM_Rev 3_AB0 |
| 16 | VA2-XG02-P0PAC-120001 | CWP_P&ID_Rev 3_AB1 |
| 17 | VA2-YR05-P1ZEN-350004 VA2-CT00-P0ZEN-350004 | VA2-YR05-P1ZEN-350004 VA2-CT00-P0ZEN-350004 |
| 18 | VA2-YB03-P0CRP-151131 | DCS - Internal Cable Connection Diagram |
| 19 | VA2-CV03-P1HFB-340002 | ELECTRICAL SPECIFICATION FOR COAL FEEDER |
| 20 | VA2-YR05-P1ZEN-350006 VA2-DP00-P0HLY-320450 | Complete Vendor's Specification for Control Shut off Valve of boiler BOILER DAMPER WITH ACTUATOR SPECIFICATION |
| 21 | VA2-XG02-P1HFC-310014 VA2-CT00-P0HFC-320000 VA2-YD00-P1HFC-320001 | P&I Diagram Coal Feeder & Pulverizer System O&M Manual BLR Pulverizer Pulverizer Arrangement |
| 22 | VA2-YL01-P0CCA-150011 VA2-YM03-P1ZEN-350001 | DCS IO Database for Unit INSTRUMENT LOCATION DRAWING FOR BOILER |
| 23 | VA2-DP00-P0HLY-320450 | BOILER DAMPER WITH ACTUATOR SPECIFICATION |
| 24 | VA2-CT00-P0HL-320010 | O&M Manual_BLR_Boiler FAN |
| 25 | VA2-YR05-P1ZEN-530002 | BTLD SENSOR LOCATION OVERVIEW |
| 26 | VA2-XG02-P1HT-530002 | PIPING & INSTRUMENT DIAGRAM SWFGD FGD DAMPER |
| 27 | VA2-XG02-P1HT-530004 | PIPING & INSTRUMENT DIAGRAM SWFGD ABSORBER & ABSORBER SPRAY PUMP |
| 28 | VA2-XG02-P1HT-530002 | PIPING & INSTRUMENT DIAGRAM SWFGD ABSORBER & ABSORBER SPRAY PUMP |
| 29 | VA2-XG02-P0ETK-510001 | P&ID DIAGRAM FOR ASH HANDLING SYSTEM |
| 30 | VA2-YM03-P1ZEN-350001 | INSTRUMENT LOCATION DRAWING |
| 31 | A2-YR05-P0HNY-150511 VA2-YR05-P0HNY-150521 VA2-XG02-P1QU-120001 VA2-YT01-P1QU-120003 VA2-XA00-P1QU-120001 VA2-YT02-P1HTY0-540100 VA2-XG02-P1HT-530001 VA2-CV03-P0QHQ-520101 VA2-XG02-P1HDE-520002 VA2-YT02-P1HS-540301 VA2-XG02-P1HSD-540003 VA2-XG02-P0LD-120001 PID VA2-YT01-P0LD-120006 | CEMS - Technical Specification Datasheet CEMS - System Configuration Drawing Sampling System P&ID Sampling System Instrument Data Sheet Sampling System General Arrangement Drawing Specification Of Gas Analyzer For FGD P&ID SWFGD Flue Gas Path Specification Of Dust Analyzer For ESP P&ID Diagram For ESP Specification Of Gas Analyzer For SCR P&ID SCR Reactor System P&ID For Condensate Polishing Plant CPP - Instrument Data Sheet |
| 32 | VA2-YR05-P1ZEN-350003 VA2-CT00-P0ZEN-350003 VA2-XG02-P1HNA-310010 | Specification For O2 Analyzer Of Boiler O&M Manual O2 Analyzer Of Boiler P&ID Boiler Flue Gas System |
| 33 | VA2-UE00-P0UP-130001 | GA_CW Pump Station Area_Rev 1_AB0 |

Annex 02_ PROPOSAL FORM

PHỤ LỤC 02_ BIỂU MẪU BẢN CHÀO GIÁ

(Company letterhead/Tiêu đề công ty)

Date/ Ngày tháng:

To: VUNG ANG II THERMAL POWER LLC (VAPCO)

Kính gửi: CÔNG TY TNHH NHIỆT ĐIỆN VŨNG ÁNG II (VAPCO)

Attn: Mr. Pham Ngoc Thach, Procurement & Contract Leader

Attn: Mr. Ha Jong Woo– GA & Contract Manager

We, _____(your company name)_______, undersigned, hereby offer to supply Unit 1 overhaul services- Instrument and Controls to Vung Ang II Thermal Power LLC in compliance with VAPCO’s RFP #VAPCO/PS-50182-3 dated 15 April 2026.

Chúng tôi, ____(tên đơn vị)________, ký tên dưới đây, chào giá cung cấp các dịch vụ tiểu tu Tổ máy 1-  Thiết bị đo lường và Điều khiển cho Công ty TNHH Nhiệt điện Vũng Áng II tuân thủ Yêu cầu chào giá của VAPCO số VAPCO/PS-50182-3 ngày 15/04/2026.

| No. Số | Item* Hạng mục | Unit and Quantity Đơn vị và Số lượng | Completion time Thời gian hoàn thành | Unit price Đơn giá (VND) | Total price Thành tiền (VND) |
| --- | --- | --- | --- | --- | --- |
| I |  |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| … |  |  |  |  |  |
| Total Price (excluding VAT)/ Tổng Giá trị (chưa bao gồm VAT) |  |  |  |  |  |

* Bidders to quote the corresponding items covered under each item of the Scope of Service

- Terms and conditions/ Các điều khoản và điều kiện:

The price is exclusive VAT but inclusive of all applicable taxes, duties or other applicable expenses

Giá chưa bao gồm thuế GTGT nhưng đã bao gồm các loại thuế, phí và các chi phí liên quan khác.

Total payment will be made within 30 days of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Contact Person/ Đầu mối liên hệ:

Contact person	:			Position

Đầu mối liên hệ: 			Chức danh

Telephone	: 			Email:

Số điện thoại: 				Email:

|  | Legal representative of Bidder Người đại diện pháp lý của Nhà thầu [Full name, position, signature and seal [Họ tên, chức vụ, chữ ký và con dấu] |
| --- | --- |

Annex 03_ CONTRACT FORM

PHỤ LỤC 03_ MẪU HỢP ĐỒNG

(from the next page/ từ trang sau)