[ATTACHMENT 1]

REQUEST FOR PROPOSAL

THƯ MỜI CHÀO GIÁ

Ref: VAPCO/PS-50182-4

To: Potential Bidders

Copy to:

Subject: Supply of minor overhaul services- Coal Handling System (CHS)/ Cung cấp các dịch vụ tiểu tu – Dây chuyền than (CHS)

- Date: 15 April 2026/ Ngày 15/04/2026

- InstructionS to the participating bidders

Chỉ dẫn đối với các nhà thầu tham gia

  - General information

Thông tin chung

Vung Ang II Thermal Power LLC (VAPCO), the Owner of 2 x 600MW ultra super-critical imported coal-fired thermal Power Plant in Vung Ang Ward, Ha Tinh Province, Vietnam that is being undertaken on a build-operate-transfer basis under Vietnam law, issuing this Request for Proposal (RFP) to invite bidders, who are interested in contracting with VAPCO for the supply of CHS minor overhaul services as detailed in Annex 01.

Công ty TNHH Nhiệt điện Vũng Áng II (VAPCO), Chủ đầu tư Nhà máy Nhiệt điện đốt than nhập khẩu trên siêu tới hạn với công suất 2 x 600MW tại phường Vũng Áng, tỉnh Hà Tĩnh, Việt Nam đang thực hiện dự án xây dựng-kinh doanh-chuyển giao theo pháp luật Việt Nam, ban hành Thư mời chào giá (RFP) này để mời các Nhà thầu quan tâm đến việc ký hợp đồng với VAPCO để cung cấp dịch vụ tiểu tu Hệ thống vận chuyển than với mô tả chi tiết như ở Phụ Lục 01.

The service is expected to commence in November 2026.

Dịch vụ dự kiến được bắt đầu trong tháng 11 năm 2026.

  - Compliance with RFP requirements

Tuân thủ các yêu cầu của Thư mời chào giá

The participating bidders shall prepare and submit a Proposal in compliance with the procedures and requirements as outlined in this RFP.  Any omission may give VAPCO a reason to reject or unfavorable evaluation of the Proposal. The participating bidders will be deemed to have fully understood and accepted all the contents of the RFP. Upon submission of a Proposal, the bidders are deemed to have agreed to fully comply with the Contract’s General Terms and Conditions as attached to the RFP.

Các bên tham gia sẽ chuẩn bị và nộp Bản chào tuân thủ các quy trình và yêu cầu như được quy định trong Thư mời chào giá này. Bất kỳ sự sai sót nào có thể khiến VAPCO có lý do từ chối hoặc đánh giá bất lợi cho báo giá. Các bên tham gia sẽ được coi là đã hiểu hoàn toàn và chấp nhận tất cả các nội dung trong Thư mời chào giá. Sau khi nộp Bản chào, khi đó thầu được coi là đã đồng ý tuân thủ đầy đủ các Điều khoản và Điều kiện chính của Hợp đồng như được đính kèm trong Thư mời chào giá.

  - Confidentiality

Bảo mật

The prices in the Proposal must be issued independently, and not be consulted, communicated, or negotiated with any other bidders.

Các giá trong Bản chào của nhà thầu phải được chào độc lập, không được tham khảo, liên lạc hoặc thỏa thuận với bất kỳ nhà thầu nào khác;

The prices stated in the Proposal have not been intentionally disclosed by the bidder and will not be knowingly disclosed, directly or indirectly, to any other participant before the Proposal submission deadline. Furthermore, these prices have not been used, and will not be used, to influence or induce any other person or company to submit, refrain from submitting, or otherwise restrict competition in any way

Các mức giá nêu trong Bản chào chưa từng được nhà thầu cố ý tiết lộ và sẽ không được tiết lộ có chủ đích, trực tiếp hoặc gián tiếp, cho bất kỳ bên tham gia nào khác trước thời hạn nộp Bản chào. Hơn nữa, các mức giá này chưa từng và sẽ không được sử dụng để tác động hoặc lôi kéo bất kỳ cá nhân hay công ty nào nộp, không nộp hồ sơ hoặc hạn chế cạnh tranh dưới bất kỳ hình thức nào.

Participating bidders must not disclose the RFP to any third parties who are not directly involved in the preparation of the Proposal.

Những người tham gia không được tiết lộ Thư mời chào giá cho bất kỳ bên thứ ba nào không liên quan trực tiếp đến việc làm báo giá.

  - Withdrawal of procurement

Thu hồi yêu cầu mua sắm

VAPCO reserves the right, at any time and without any liability to the participants, to cancel, delay or extend this procedure or to change the scope of the procurement.

VAPCO có quyền, bất cứ lúc nào và không có bất kỳ trách nhiệm nào đối với các bên tham gia, trong việc hủy bỏ, trì hoãn hoặc gia hạn thủ tục này hoặc thay đổi phạm vi mua sắm.

  - Language

Ngôn ngữ

The documents shall be prepared in English and Vietnamese. If there is any difference or inconsistency between English and Vietnamese, the English language shall prevail.

Các tài liệu được chuẩn bị bằng tiếng Anh và tiếng Việt. Nếu có bất kỳ sự khác biệt hoặc mâu thuẫn nào giữa tiếng Anh và tiếng Việt thì bản tiếng Anh sẽ được áp dụng.

  - Currency and Payment

Tiền tệ và thanh toán

The price shall be quoted in Vietnamese Dong, exclusive of VAT.

Giá được chào giá bằng đồng Việt Nam, chưa bao gồm thuế GTGT

Payment shall be made in Vietnamese Dong.

Thanh toán được thực hiện bằng đồng Việt Nam.

- Procedures for RFP

Thủ tục mời chào giá

  - Clarification of bidding information

Làm rõ thông tin mời thầu

The participating bidders are requested to study and carefully check the contents of the bidding information and other relevant information. The bidders may send an email to VAPCO’s PIC: Mr. Pham Ngoc Thach, at thach.pham@vapco.com.vn (copying: Mr. Ha Jong Woo, at jeff.ha@vapco.com.vn) or an official letter to VAPCO regarding the unclear contents at least 5 days before the due date of letter of Proposal submission. Written clarifications or feedback via email (as the case may be) will be provided by VAPCO no later than 1 day before the due date of Proposal submission.

Nhà thầu tham gia được yêu cầu nghiên cứu và kiểm tra kỹ lưỡng nội dung của thông tin mời thầu và các thông tin liên quan khác. Các Nhà thầu có thể gửi email cho VAPCO: Ông Phạm Ngọc Thạch theo địa chỉ thach.pham@vapco.com.vn (cc cho ông Ha Jong Woo tại jeff.ha@vapco.com.vn) hoặc thư chính thức đến VAPCO về các nội dung không rõ ít nhất 5 ngày trước ngày hết hạn nộp Hồ sơ chào giá. Giải thích bằng văn bản hoặc phản hồi bằng email (tuỳ trường hợp cụ thể) sẽ được VAPCO cung cấp không muộn hơn 1 ngày hết hạn nộp bản chào.

At any time, before 3 days before the due date of Proposal submission, VAPCO has the right to amend or add to the bidding information. The amendment or supplement shall be communicated in writing to all participating bidders and the bidders shall be obliged to comply with such addition or amendment.

Vào bất kỳ thời điểm nào trước khi hết hạn nộp hồ sơ chào giá 3 ngày. VAPCO có quyền sửa đổi, bổ sung thông tin mời thầu. Việc sửa đổi, bổ sung sẽ được thông báo bằng văn bản tới tất cả các nhà thầu tham gia và các nhà thầu có nghĩa vụ tuân thủ việc bổ sung, sửa đổi đó.

  - Submission of Proposal

Nộp Bản chào

Each bidder will finalize and fill out the form given in Item 4.

Mỗi nhà thầu tham gia sẽ hoàn thiện và điền vào biểu mẫu tại Mục 4.

Bidders are required to submit supporting documents for Technical Evaluation as follows:

- Certificate of business registration

- Reference contracts and completion certificates to supply overhaul services to thermal power plants for the last 7 years

- Work Method Statement inluding detailed overhaul execution plan and heavy equipment and tools deployment plan

- Quality assurance and control plan and procedures

- Risk Assessment Report for technical risk identification and mitigation

- CV of the Project Manager and key engineers showing qualification and overhaul experience

- Detailed schedule at Primavera/ MS Project Level

- Delay Recovery Plan with acceleration strategy

- HSSE Policy, Plan and Procedures

- Safety record showing LTIR/TRIR for the last 3 years

Các nhà thầu phải nộp các giấy tờ chứng minh cho mục đích Đánh giá kỹ thuật như sau:

- Giấy đăng ký kinh doanh của nhà thầu

- Các hợp đồng và chứng nhận hoàn thành tham chiếu cho việc cung cấp dịch vụ kỹ thuật bảo trì cho nhà máy nhiệt điện trong vòng 7 năm qua

- Thuyết minh biện pháp thi công bao gồm kế hoạch triển khai công việc và kế hoạch huy động phương tiện, thiết bị và dụng cụ

- Kế hoạch và quy trình kiểm soát và đảm bảo chất lượng

- Báo cáo đánh giá rủi ro nhằm nhận diện và hạn chế các rủi ro kỹ thuật

- CV của Quản lý dự án và các kỹ sư chính nêu rõ bằng cấp và kinh nghiệm trong tiểu tu

- Bảng tiến độ công việc chi tiết trên nền tảng Primavera/ MS Project Level

- Kế hoạch phục hồi sau gián đoạn với chiến lược tăng tốc

- Chính sách, Kế hoạch và Các quy trình HSSE

- Hồ sơ an toàn bao gồm các thông tin về LTIR/TRIR trong 3 năm qua

Bidders are required to attach a Letter of Confirmation that by submitting the Proposal, they have understood and accepted all major terms and conditions of Part III- Key Terms and Conditions, Annex 01- Scope of Service, and Annex 03- Contract Form of this RFP.

Các nhà thầu phải đính kèm Thư xác nhận rằng bằng việc nộp Thư chào giá, họ đã hiểu và chấp nhận các điều kiện và điều khoản chính của Phần III- Điều kiện và Điều khoản chính, Phụ lục 01- Phạm vi Dịch vụ và Phụ lục 03- Mẫu hợp đồng.

The Proposal Form and other documents shall be submitted by email to the following address no later than the deadline to:

Bản chào sẽ được gửi bằng email đến địa chỉ sau không muộn hơn thời hạn:

Mr. Pham Ngoc Thach / Procurement & Contract Leader,

Vung Ang II Thermal Power LLC,

Address : Vung Ang Economic Zone, Vung Ang Ward, Ha Tinh,

Email: thach.pham@vapco.com.vn,  Phone No: 0986040681,

Copying: Mr. Ha Jong Woo, GA & Contract Manager,

Email: jeff.ha@vapco.com.vn.

The Proposal Form will be encrypted to ensure that it won’t be opened before the time specified in Item 3 below.

Bản chào giá sẽ được mã hóa nhằm đảm bảo không được mở trước thời gian quy định trong Điều 3 sau đây.

Email subject: The bidders are kindly requested to clearly state the bidding package’s name and the bidder's name (e.g.: "Proposal for supply of Unit 1 minor overhaul services / "Bidder's name").

Tiêu đề thư: Nhà thầu ghi rõ tên gói thầu và tên nhà thầu (ví dụ: “Bản chào cho việc cung cấp dịch vụ tiểu tu Tổ máy 1 / "Tên nhà thầu”).

(The bidder may contact Mr. Pham Ngoc Thach for confirmation of the sent email/ Nhà thầu có thể liên hệ với Ông Phạm Ngọc Thạch để xác nhận email đã gửi thành công).

  - Deadline for submission of the Proposal

Thời hạn nộp bản chào giá:

The due date for Proposal submission is 17:00, 07 May 2026

Ngày hết hạn nộp bản chào giá: 17:00, ngày 07/05/2026

The bidder will share the password to open the pdf file of the Proposal Form via email by 09:00, 08 May 2026.

Nhà thầu sẽ gửi mật khẩu để mở Bản chào giá qua email vào 9:00 ngày 08/05/2026.

  - Validity period

Thời hạn hiệu lực

The Proposal shall be offered and valid for 120 days from the due date of Proposal document submission. VAPCO may request to extend the validity time of the Proposal and notify it in writing. The extension time shall not exceed 15 days. If the bidder fails to accept the extension of the validity time, its Proposal will not be considered for evaluation.

Chào giá được đưa ra và có hiệu lực trong vòng 120 ngày kể từ ngày hết hạn nộp hồ sơ chào giá. VAPCO có thể yêu cầu gia hạn thời gian hiệu lực của chào giá và thông báo bằng văn bản, thời gian gia hạn sẽ không vượt quá 15 ngày. Trường hợp nhà thầu tham gia không chấp nhận gia hạn thời gian hiệu lực thì chào giá đó sẽ không được xem xét để đánh giá.

  - Bid evaluation and award criteria

Tiêu chí đánh giá hồ sơ dự thầu và lựa chọn

Proposal evaluation

Đánh giá Bản chào

The bidders' Proposal will be considered and evaluated when they fully meet the above criteria, and the document is submitted as prescribed in Item 2.2 before the deadline or subject to VAPCO’s decision.

Bản chào của Nhà thầu chỉ được xem xét đánh giá khi đáp ứng đầy đủ các tiêu chí nêu trên và nộp bộ hồ sơ như quy định tại Mục 2.2 trước thời điểm đóng thầu hoặc theo quyết định của VAPCO.

- Technical evaluation

Đánh giá về kỹ thuật

- Financial evaluation:

Đánh giá về tài chính

The bidder with the highest combined score from both technical and financial evaluations will be selected as the preferred bidder and invited to enter the contract negotiation stage.

Nhà thầu nào đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính sẽ được chọn vào giai đoạn thương thảo hợp đồng.

- Award Criteria

Tiêu chí lựa chọn

VAPCO will award the Contract to the bidder with the highest combined score from both technical and financial evaluations and favourable terms after negotiation.

VAPCO sẽ ký hợp đồng với Nhà thầu đạt được tổng điểm cao nhất kết hợp giữa đánh giá kỹ thuật và tài chính và các điều khoản phù hợp nhất sau khi đàm phán.

VAPCO has the right to adjust the Scope of Service at its discretion.

VAPCO có thể điều chỉnh Phạm vi Dịch vụ theo quyền quyết định của mình.

  - Announcement of evaluation result

Thông báo kết quả đánh giá

The evaluation result might be announced to all participants after the decision on approval of the result. In the notice of the evaluation result, VAPCO is not obligated to explain the reasons for the unsuccessful bidders.

Kết quả đánh giá có thể được thông báo cho các bên tham gia sau khi có quyết định phê duyệt kết quả đánh giá cuối cùng. Trong thông báo kết quả đánh giá, VAPCO không có nghĩa vụ giải thích lý do đối với các nhà thầu không được lựa chọn.

  - VAPCO’s option

Tùy chọn của VAPCO

VAPCO reserves the right, without any liability to the parties, to modify or withdraw this RFP at any time, to increase or decrease the Scope of Service included in the Contract or request to restart the procedure when deemed valid is of the greatest interest to VAPCO and rejects any or all the Proposals. No claim regarding any modification, withdrawal, or restart of the process will be accepted by VAPCO. VAPCO also has the option to award the Contract to an acceptable participant, whichever is in the best interest of the company.

VAPCO bảo lưu quyền, mà không có bất kỳ trách nhiệm nào đối với các bên tham gia, sửa đổi hoặc rút lại Yêu cầu chào giá này bất cứ lúc nào, để tăng hoặc giảm phạm vi công việc được đưa vào Hợp đồng hoặc yêu cầu khởi động lại thủ tục khi được coi là hợp lệ được VAPCO quan tâm nhất và từ chối bất kỳ hoặc tất cả các đề xuất. Không có yêu cầu bồi thường liên quan đến bất kỳ sửa đổi, rút lui hoặc khởi động lại quá trình sẽ được VAPCO chấp nhận. VAPCO cũng có tùy chọn để trao hợp đồng cho bên tham gia chấp nhận được, tùy theo điều kiện nào là tốt nhất cho lợi ích của công ty.

  - Compliance in bidding

Tuân thủ trong đấu thầu

The bidders must comply with the provisions of the law on anti-corruption, anti-bribery, and anti-monopoly and commit to bidding standards to ensure healthy competition, fairness, and transparency.

Các nhà thầu phải tuân thủ các quy định của pháp luật về phòng chống tham nhũng, chống hối lộ, chống độc quyền và cam kết các tiêu chuẩn đấu thầu đảm bảo cạnh tranh lành mạnh, công bằng và minh bạch.

- Key terms and conditions

Điều khoản và điều kiện chính

  - Contract term

Thời hạn Hợp đồng

The Contract shall come into effect upon signing and shall remain in force until both parties have fulfilled their contractual obligations.

Hợp đồng sẽ có hiệu lực kể từ ngày ký và sẽ có hiệu lực cho đến khi hai bên hoàn thành nghĩa vụ theo hợp đồng

  - Contract price

Giá trị Hợp đồng

The Contract price is based on a fixed-unit price.

Giá trị Hợp đồng được tính trên cơ sở đơn giá cố định.

  - Payment

Thanh toán

Total payment will be made within 30 days from the date of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Proposal form

Mẫu bản chào giá

Bidders are encouraged to submit their Proposals using the following form as per Annex 02.

Nhà thầu được khuyến nghị nộp bản chào theo mẫu ở Phụ Lục 02 sau đây.

Annex 01_ SCOPE OF SERVICE

PHỤ LỤC 01_ phạm vi DỊCH VỤ

- Scope of overhaul maintenance services for Lot 4 (Coal Handling System)

| No. | Item | Work description | Unit | Qtty |
| --- | --- | --- | --- | --- |
| 1 | Technical Supervisor | Supervise technical package, prepare all documents | Pack | 1 |
| 2 | Safety Supervisor | Supervise safety for package and prepare PTW | Pack | 1 |
| 3 | Ship Unloader gantry Drive Device - Gantry Reducer | 1. Drain all gearbox oil. Dismantle the motor and gearbox, remove the motor foundation bolts, and take out the old gearbox. 2. Inspect the condition of the gears, measure gear wear, and check the clearance and wear of the bearings. 3. Replace excessively worn components or damaged gears, and replace all oil seals. 4. Thoroughly clean all parts, apply gasket sealant, and tighten all flanges. 5. Install the new (or repaired) gearbox and reinstall the motor. Perform alignment to ensure proper concentricity. 6. Reconnect the power supply cables. 7. Refill with new lubricating oil. 8. Conduct a trial run and carry out inspection to ensure normal operation. | Set | 40 |
| 4 | Ship Unloader Machinery House - Boom hoist reducer | 1. Drain all gearbox lubricating oil. 2. Dismantle the motor and gearbox, remove the motor foundation bolts, and take out the existing/old gearbox. 3. Inspect the condition of the gears, check for wear or damage, and measure the clearance and wear of the bearings. 4. Replace all defective components, including worn or broken gears, bearings, and all oil seals. 5. Thoroughly clean all parts, apply gasket sealant, and tighten all flanges. 6. Install the repaired or new gearbox and reinstall the motor. 7. Perform alignment to ensure proper concentricity between the motor and gearbox. 8. Tighten all foundation bolts and reconnect the power supply cables. 9. Refill with new lubricating oil. 10. Energize the system and conduct a trial run for inspection. | Set | 2 |
| 5 | Ship Unloader Machinery House - Main hoist and trolley reducer | 1. Drain all gearbox lubricating oil. 2. Dismantle the motor and gearbox, remove the motor foundation bolts, and take out the existing/old gearbox. 3. Inspect the condition of the gears, check for wear or damage, and measure the clearance and wear of the bearings. 4. Replace all defective components, including worn or broken gears, bearings, and all oil seals. 5. Thoroughly clean all parts, apply gasket sealant, and tighten all flanges. 6. Install the repaired or new gearbox and reinstall the motor. 7. Perform alignment to ensure proper concentricity between the motor and gearbox. 8. Tighten all foundation bolts and reconnect the power supply cables. 9. Refill with new lubricating oil. 10. Energize the system and conduct a trial run for inspection. | Set | 2 |
| 6 | Ship Unloader Machinery House - Bearing | 1. Secure the cable drum shaft. 2. Dismantle and remove the bearings, and inspect for wear, pitting, or damage. 3. Replace all excessively worn or damaged bearings with new ones. 4. Apply proper lubrication to the bearings. 5. Reinstall the bearings and carry out proper alignment. | Set | 8 |
| 7 | Ship Unloader Machinery House - Drum Coupling | 1. Clean and inspect the entire grease lubrication piping system. 2. Replace damaged fittings and pipelines. 3. Pump new grease to replace the old grease. | Set | 76 |
| 8 | Ship Unloader Machinery House - Luffing Brake Hydraulic System | 1. Drain the oil from the hydraulic brake system of the boom lifting system, and inspect and replace the gasket if necessary. 2. Refill with new hydraulic oil, inspect, and conduct a trial run. | Set | 2 |
| 9 | Ship Unloader Hopper System - Belt conveyorreducer | 1. Drain all gearbox lubricating oil. 2. Dismantle the motor and gearbox. 3. Inspect the condition of the gears and measure the clearance and wear of the bearings. 4. Replace all defective components, including worn or broken gears, bearings, and all oil seals. 5. Thoroughly clean all parts, apply gasket sealant, and tighten all flanges. 6. Reinstall the gearbox and motor. 7. Perform alignment to ensure proper concentricity. 8. Tighten all foundation bolts. 9. Refill with new lubricating oil. 10. Energize the system and conduct a trial run for inspection. | Set | 2 |
| 10 | Ship Unloader Hopper System - Belt feeder | 1. Inspect the condition of the conveyor belt and measure its hardness. 2. Dismantle the frame, discharge chute, and roller system if replacement is required. 3. Replace the worn conveyor belt. 4. Reinstall all components and carry out proper alignment. 5. Conduct a trial run to ensure normal operation. | Set | 2 |
| 11 | Ship Unloader Boom - Hoisting/closing device pulley block and rope | 1. Dismantle the wire rope system and remove the pulley assembly. 2. Measure the wear of the pulley and bearings, and replace them if damaged. 3. Inspect the wear condition and re-reeve the wire rope system, replacing it if necessary. 4. Lubricate and reinstall. | Set | 5 |
| 12 | Ship Unloader Boom - Catenary trolley pulley block | 1. Inspect the wire rope for wear and broken strands, and replace it if necessary. 2. Lubricate the entire wire rope and refill grease for the automatic greasing units. | Set | 4 |
| 13 | Ship Unloader Boom - Forestay front hinge point and pulley block | 1. Dismantle and measure the wear of the pulley, inspect the bearing wear, and replace them if worn or damaged. 2. Lubricate, reinstall, and realign properly. | Set | 5 |
| 14 | Ship Unloader Girder - Hoisting/closing device pulley block | 1. Dismantle the wire rope system and remove the pulley assembly. 2. Measure the wear of the pulley and bearings, and replace them if damaged. 3. Inspect the wear condition and re-reeve the wire rope system, replacing it if necessary. 4. Lubricate and reinstall. | Set | 4 |
| 15 | Ship Unloader Girder - Catenary trolley pulley block | 1. Dismantle the wire rope system and remove the pulley assembly. 2. Measure the wear of the pulley and bearings, and replace them if damaged. 3. Inspect the wear condition and re-reeve the wire rope system, replacing it if necessary. 4. Lubricate and reinstall. | Set | 4 |
| 16 | Ship Unloader Girder - Catenary trolley hydraulic cylinder | 1. Disassemble and inspect the wear condition of the shaft, pulley, and bearings. Replace if necessary. 2. Lubricate and reinstall. | Set | 2 |
| 17 | Ship Unloader Girder - Replace lubricating Tension pulley | 1. Disassemble, clean, and replace with new grease. | Set | 2 |
| 18 | Ship Unloader Girder - Tension pulley | 1. Disassemble and inspect the wear condition of the shaft, pulley, and bearings. Replace if necessary. 2. Lubricate and reinstall. | Set | 2 |
| 19 | Ship Unloader Trolley and Catenary Trolley - Trolley | 1. Clean and conduct a general inspection of the trolley. Check the wear condition of the guide wheels and replace if worn. 2. Tighten all bolts and apply lubrication. | Set | 28 |
| 20 | Ship Unloader Trolley and Catenary Trolley - Front catenary trolley | 1. Clean and conduct a general inspection of the trolley. Check the wear condition of the guide wheels and replace if worn. 2. Tighten all bolts and apply lubrication. | Set | 20 |
| 21 | Ship Unloader Trolley and Catenary Trolley - Back catenary trolley | 1. Clean and conduct a general inspection of the trolley. Check the wear condition of the guide wheels and replace if worn. 2. Tighten all bolts and apply lubrication. | Set | 20 |
| 22 | Ship Unloader Grab Bucket - Grab Bucket | 1. Inspect all grease nipples and check the shaft condition. Apply new grease or replace if necessary. | Set | 36 |
| 23 | Ship Unloader Grab Bucket - Grab bucket guide | 1. Disassemble the guides and inspect the bearings. Replace any bearings that are excessively worn or damaged. 2. Reinstall and realign. | Set | 8 |
| 24 | Ship Unloader Grab Bucket - Bucket mechanical frame | 1. Scaffolding was erected and all old paint was removed. 2. Primer and top coat were applied to the entire surface. 3. Scaffolding was dismantled and final cleaning was completed. | Set | 2 |
| 25 | STACKER - RECLAIMER A/B - Slewing System | 1. Erect scaffolding and remove the protective cover. 2. Inspect the condition and wear of the gears and other mechanical components. 3. Replace all excessively worn gears and defective components. 4. Replace the hydraulic oil. 5. Reinstall all components. 6. Conduct a test run and carry out inspection to ensure normal operation. | Set | 2 |
| 26 | STACKER - RECLAIMER A/B - Buckets | 1. Erect scaffolding and disconnect all electrical wiring, hydraulic pipelines, bearings, and support housings. 2. Use a crane to dismantle the old bucket and carry out a general inspection. If excessive damage is found, proceed with replacing it with a new bucket. 3. Remove all existing wear plates. 4. Install new wear plates and replace all worn components. 5. Tighten all bolts and carry out proper alignment to ensure concentricity. 6. Reconnect all electrical cables and hydraulic oil pipelines. 7. Conduct a test run for inspection to ensure normal operation. | Set | 2 |
| 27 | STACKER - RECLAIMER A/B - Bucket wheel shaft | 1. Install scaffolding and secure the bucket. 2. Inspect the condition of the shaft and replace it if any bending or damage is detected. 3. Dismantle and inspect the bearings, and replace them if they are damaged or exhibit excessive play. 4. Remove the old shaft and bearings. 5. Install the new shaft and new bearings. 6. Apply proper lubrication. 7. Perform alignment and ensure all components are correctly positioned. 8. Tighten and secure all components. | Set | 2 |
| 28 | STACKER - RECLAIMER A/B - Buckets wheel bearing | 1. Dismantle and inspect the bearings for contamination, dirt, and discoloration caused by overheating. Replace any defective or poor-quality bearings 2. Prepare the required tools, materials, and crane for the bearing replacement work. 3. Replace the bearings with new ones. 4. Replace the old oil and grease with new lubricants. | Set | 2 |
| 29 | STACKER - RECLAIMER A/B - Hydraulic Driver (110 kW) | 1. Inspection: Check for external oil leakage. Inspect te condition of the shaft seals. 2. Measurement: Measure the case drain flow. Measure the operating pressure. 3. Checking: Check for abnormal noise or vibration. 4. Disassembly and Inspection: Disassemble the unit and inspect all internal components for damage. 5. Repair/Replacement: Repair or replace any damaged parts as necessary. Replace seals if any leakage is detected. 6. Replacement (if required): Replace the hydraulic pump/motor with a new unit if performance is degraded or damage is beyond repair. | Set | 2 |
| 30 | STACKER - RECLAIMER A/B - Hydraulic Hoses & Pipes | 1. Remove the cover. 2. Clean all hydraulic oil lines thoroughly. 3. Replace all O-rings. 4. Apply Teflon tape to threaded connections and tighten all hydraulic oil lines. 5. Drain and replace all old oil with new hydraulic oil. | Set | 2 |
| 31 | STACKER - RECLAIMER A/B - Luffing System | 1. Inspect hydraulic cylinders or hoisting winches. 2. Inspect wire ropes, pulleys, and drums. 3. Inspect pins and bushings. 4. Inspect the luffing travel range and limit settings. 5. Replace all old oil in the lifting system with new oil. | Set | 2 |
| 32 | STACKER - RECLAIMER A/B - Intermediate Conveyor, Boom Convey | 1. Inspect the condition of the automatic grease piping system for pulley bearings; check the bearings and replace them if worn or loose. 2. Inspect the carrying and return idler assemblies; replace any worn or damaged rollers, tighten all components, and replace any defective bolts. 3. Inspect and adjust the idler assembly of the belt scale; repair or replace the supporting frame if necessary. | Set | 2 |
| 33 | STACKER - RECLAIMER A/B - Skirt Rubber and Sealing System | 1. Remove all bolts and dismantle the existing skirt of the Stacker A/B conveyor belt. 2. Clean the work area. 3. Measure and cut the new skirt to the required dimensions. 4. Position and install the new skirt, ensuring proper alignment. 5. Tighten all bolts securely. 6. Clean the work area after completion. | Set | 2 |
| 34 | STACKER - RECLAIMER A/B - Transfer Chutes and Inspection Doors | 1. Inspect chute wear, blockage, and material leakagInspect wear liners (steel). Inspect inspection doors and sealing gaskets. 2. Welding repair, liner replacement, gasket replacement. | Set | 2 |
| 35 | STACKER - RECLAIMER A/B - Belt Cleaning Devices (Primary / Secondary Cleaners) | 1. Cleaning, disassembling, repairing, or replacing all conveyor belt cleaning blades, reinstalling the blades, cleaning the work area after completion. | Set | 2 |
| 36 | STACKER - RECLAIMER A/B - Hydraulic System | 1. Clean the hydraulic pump, valves, and cylinders.- Check oil leakage and operating pressure Inspect hydraulic oil filters. 2. Filter replacement, seal replacement, oil replenishment or change. 3. Installation & Testing. | Set | 2 |
| 37 | STACKER - RECLAIMER A/B - Boom Conveyor Drive System (Motor – Gearbox – Coupling) | 1. Cleaning the gearbox and surrounding area to remove dirt, dust, and oil contamination. 2. Removing the gearbox cover carefully to access internal components for inspection and maintenance. 3. Draining the old oil completely from the gearbox to eliminate contaminants and degraded lubricant. 4. Replacing worn or damaged bearings to ensure smooth rotation and reliable operation. 5. Replacing damaged or aged gearbox seals to prevent oil leakage and maintain proper sealing. 6. Changing the fluid coupling oil to maintain proper torque transmission and cooling performance. 7. Changing the motor oil to ensure proper lubrication and extend the service life of the motor. 8. Readjusting the gearbox alignment and settings to ensure proper operation and load distribution. 9. Readjusting the motor alignment with the gearbox to ensure correct coupling and reduce vibration. | Set | 2 |
| 38 | STACKER - RECLAIMER A/B - Intermediate conveyor. | 1. Dismantling Work Dismantle approximately 4 meters of the roller frame to prepare for the installation of the new conveyor belt. Remove the intermediate pulley alignment bolts to release belt tension, and dismantle the primary and secondary cleaner blades. A crane will be required to remove the existing conveyor belt and lift the new belt onto the conveyor structure for installation along the entire conveyor length. 2. Belt Installation and Splicing After positioning the new conveyor belt, prepare the required materials and equipment, including adhesive, steel frame, and heat press machine. Proceed with belt splicing using the hot vulcanizing method. 3. Replace 2 take-up pulley bearings and 2 drive pulley bearings. 4. Reassembly and Alignment Upon completion of belt installation, reassemble the roller frame and conveyor rollers, reinstall the primary and secondary cleaner blades, and properly align and tension the conveyor belt to ensure stable and safe operation. | Set | 2 |
| 39 | STACKER - RECLAIMER A/B - Boom conveyor | 1.Dismantling Work Dismantle 4 meters of the roller frame to prepare for the installation of the conveyor belt floor. Remove the boom conveyor pulley alignment bolts to loosen the belt, and remove the primary and secondary cleaner blades. A crane is required to remove the old conveyor belt and lift the new belt onto the conveyor structure for installation along the entire conveyor length. 2. Belt Installation and Splicing After positioning the conveyor belt, prepare necessary materials such as adhesive, steel frame, and heat press machine, then proceed with belt splicing. 3. Replace 2 take-up pulley bearings and 2 drive pulley bearings. 4. Reassembly and Alignment Upon completion of belt installation, reassemble the roller frame and conveyor rollers, reinstall the primary and secondary cleaner blades, and properly realign the conveyor belt to ensure stable operation. | Set | 2 |
| 40 | JV-01 CONVEYOR - Seal Belt | Replace seal belt ( Replace for 1.jiont) 1. Stop the conveyor, perform LOTO, clean coal 2. Release tension, cut and remove old belt 3. Install new belt into the system 4. Prepare splice ends (step cutting, ply stripping, buffing, cleaning) 5. Apply cement and arrange rubber layers 6. Perform hot vulcanization (temperature, pressure, time as per standard) 7. Cool down and inspect splice 8. Tension the belt and adjust tracking 9. Test run 10. Inspect and hand over | Set | 1 |
| 41 | JV-01 CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 247M with 18 joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 42 | JV-01 CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 9 |
| 43 | JV-01 CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 18 |
| 44 | JV-01 CONVEYOR - Ilder | Dismantle the cover: Dismantling the cover 1.Preparation work: isolate power supply, place warning tags, and prepare tools. 2. Remove bolts/nuts securing the cover. 3. Use lifting equipment if required and carefully remove the cover from its position. 4. Place the cover in a safe location to prevent deformation or damage. Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. Reinstalling the cover: 1.Inspect the condition of the cover and installation area. 2. Position the cover correctly in its original location. 3.Reinstall and tighten all bolts/nuts to the required torque. 4. Check stability and conduct a trial run. | Pack | 1 |
| 45 | JV-01 CONVEYOR - Belt Cleaning Devices (Primary / Secondary Cleaners) | Replace Primary Cleaner : 1.Isolate power supply, apply LOTO, and prepare necessary tools. 2. Loosen the tensioning mechanism to release blade pressure. 3. Remove the worn blade from the holder. 4. Install the new blade in the correct position and secure it firmly. 5.Adjust the blade pressure according to technical specifications. 6. Inspect and conduct a trial run of the conveyor. Replace Secondary : 1.Isolate power supply, apply LOTO, and prepare necessary tools. 2. Loosen the tensioning mechanism to release blade pressure. 3. Remove the worn blade from the holder. 4. Install the new blade in the correct position and secure it firmly. 5.Adjust the blade pressure according to technical specifications. 6. Inspect and conduct a trial run of the conveyor. | Set | 2 |
| 46 | JV-01 CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools, and ensure safety (LOTO applied). 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 1 |
| 47 | JV-01 CONVEYOR - Gear Box B214HSB-C14+UF21-ZF21518 | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 3 |
| 48 | JV-01 CONVEYOR - Fluid Coupling YOTCS - 750B | Inspect Fluid couplings : 1.Stop the machine and ensure safety. 2. Check for oil leakage, loose bolts, and casing condition. 3. Check oil level and oil condition. 4. Check vibration and abnormal noise during operation. 5.Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1.Stop the machine and perform LOTO. 2. Drain all old oil and inspect its condition. 3. Reinstall and tighten the drain plug. 4. Fill with the correct type and level of oil. 5.Perform a test run and check for leaks. Replace Fruid Coupling : 1.Stop the machine and drain the coupling oil. 2. Remove the old coupling and inspect the shaft. 3. Install the new coupling and tighten properly. 4. Fill with the correct type and amount of oil. 5.Align and perform a test run. | Set | 3 |
| 49 | JV-01 CONVEYOR - Brake YWZ9-630 - TH III - 3006 | Inspection 1. Stop the system and perform LOTO. 2. Check overall condition (cracks, looseness, dirt). 3. Check brake pad wear and condition. 4. Measure and verify brake air gap. 5. Inspect brake disc/drum surface (wear, scoring, damage). 6. Check brake mechanism (spring, rod, movement, jamming). 7. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 8. Perform test run and evaluate braking performance (response, holding capacity). 9. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts, and ensure safety (LOTO). 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Stop the conveyor and perform LOTO. 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 3 |
| 50 | JV-01 CONVEYOR - Gear Coupling TY - SB - 250 | Inspection 1. Prepare and ensure safety, perform LOTO. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Stop equipment and perform LOTO. 2. Clean the coupling area and remove the cover. 3. Inspect internal condition of gears and seals. 4. Apply specified grease with correct type and quantity. 5. Reinstall the cover and tighten bolts securely. 6 Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts, and ensure safety (LOTO). 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 3 |
| 51 | CV 01 AB CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 247M with 18 joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 52 | CV 01 AB CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 10 |
| 53 | CV 01 AB CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 20 |
| 54 | CV 01 AB CONVEYOR - Ilder | Dismantle the cover: Dismantling the cover 1.Preparation work: isolate power supply, place warning tags, and prepare tools. 2. Remove bolts/nuts securing the cover. 3. Use lifting equipment if required and carefully remove the cover from its position. 4. Place the cover in a safe location to prevent deformation or damage. Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. Reinstalling the cover: 1.Inspect the condition of the cover and installation area. 2. Position the cover correctly in its original location. 3.Reinstall and tighten all bolts/nuts to the required torque. 4. Check stability and conduct a trial run. | Pack | 1 |
| 55 | CV 01 AB CONVEYOR - Skirt Rubber and Sealing System | Replace Skirt & Sealing : 1.Isolate the conveyor power supply, apply LOTO, and prepare materials and tools. 2.Remove the clamp bolts and dismantle the old skirt and sealing. 3.Clean the installation area thoroughly. 4.Install the new skirt in the correct position. 5.Install the new sealing and tighten all bolts securely. | Set | 2 |
| 56 | CV 01 AB CONVEYOR - Transfer Chutes and Inspection Doors | Inspection: - Transfer Chute 1. Perform LOTO and ensure safety. 2. Inspect internal wear condition. 3. Check for blockage and material buildup. 4. Inspect for leakage and spillage. 5. Record findings. - Wear Liners: 1. Perform LOTO and ensure safety. 2. Check wear condition and measure remaining thickness. 3. Inspect for cracks, delamination, and deformation. 4. Check fastening condition (bolts, looseness). 5. Verify liner fit-up, gap, and alignment. - Doors & Sealing 1. Perform LOTO and ensure safety. 2. Check door operation and locking mechanism. 3. Inspect sealing gasket (wear, cracks, hardening). 4. Check for material leakage. Replacement - Wear Liners Replacement 1. Stop equipment and perform LOTO. 2. Remove bolts and dismantle worn liners. 3. Clean and inspect installation surface. 3. Install new liners in correct position. 4. Check alignment and fit-up. 5. Tighten bolts to specified torque. - Flow Driver Replacement 1. Prepare tools, lifting equipment, and ensure safety. 2. Stop equipment, perform LOTO, disconnect power and coupling. 3. Remove old Flow Driver. 4. Inspect and clean shaft, coupling, and base. 5. Install new unit and perform alignment. 6. Tighten bolts to specified torque. - Bearing Housing Replacement 1. Stop conveyor and perform LOTO. 2. Mark position and remove old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing. 5. Tighten locking device and bolts to specified torque. 6. Lubricate as required. Final Inspection & Test Run 1. Verify all components are properly installed and secured. 2. Check for leakage, looseness, and abnormal condition. 3. Perform test run (no load → load). 4. Monitor vibration, noise, and operating condition. 5. Confirm stable and normal operation. | Set | 2 |
| 57 | CV 01 AB CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools, and ensure safety (LOTO applied). 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 2 |
| 58 | CV 01 AB CONVEYOR - Gear Box B213HSC-C14+UF21+UB11+CW-ZF21518 | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 2 |
| 59 | CV 01 AB CONVEYOR - Fluid Coupling YOTVNZ - 875 | Inspect Fluid couplings : 1. Stop the machine and ensure safety. 2. Check for oil leakage, loose bolts, and casing condition. 3. Check oil level and oil condition. 4. Check vibration and abnormal noise during operation. 5. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Stop the machine and perform LOTO. 2. Drain all old oil and inspect its condition. 3. Reinstall and tighten the drain plug. 4. Fill with the correct type and level of oil. 5. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Stop the machine and drain the coupling oil. 2. Remove the old coupling and inspect the shaft. 3. Install the new coupling and tighten properly. 4. Fill with the correct type and amount of oil. 5. Align and perform a test run. | Set | 2 |
| 60 | CV 01 AB CONVEYOR - Brake YWZ9-630 - TH III - 3006 | Inspection 1. Stop the system and perform LOTO. 2. Check overall condition (cracks, looseness, dirt). 3. Check brake pad wear and condition. 4. Measure and verify brake air gap. 5. Inspect brake disc/drum surface (wear, scoring, damage). 6. Check brake mechanism (spring, rod, movement, jamming). 7. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 8. Perform test run and evaluate braking performance (response, holding capacity). 9. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts, and ensure safety (LOTO). 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Stop the conveyor and perform LOTO. 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 2 |
| 61 | CV 01 AB CONVEYOR - Gear Coupling TY - SB - 250 | Inspection 1. Prepare and ensure safety, perform LOTO. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Stop equipment and perform LOTO. 2. Clean the coupling area and remove the cover. 3. Inspect internal condition of gears and seals. 4. Apply specified grease with correct type and quantity. 5. Reinstall the cover and tighten bolts securely. 6 Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts, and ensure safety (LOTO). 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 2 |
| 62 | CV 02 CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 227m with 5.joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 63 | CV 02 CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 11 |
| 64 | CV 02 CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 22 |
| 65 | CV 02 CONVEYOR - Ilder | Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. | Pack | 1 |
| 66 | CV 02 CONVEYOR - Skirt Rubber and Sealing System | Replace Skirt & Sealing : 1.Prepare materials and tools. 2.Remove the clamp bolts and dismantle the old skirt and sealing. 3.Clean the installation area thoroughly. 4.Install the new skirt in the correct position. 5.Install the new sealing and tighten all bolts securely. | Pack | 1 |
| 67 | CV 02 CONVEYOR - Transfer Chutes and Inspection Doors | Inspection: - Transfer Chute 1. Inspect internal wear condition. 2. Check for blockage and material buildup. 3. Inspect for leakage and spillage. 4. Record findings. - Wear Liners: 1. Check wear condition and measure remaining thickness. 2. Inspect for cracks, delamination, and deformation. 3. Check fastening condition (bolts, looseness). 4. Verify liner fit-up, gap, and alignment. - Doors & Sealing 1. Check door operation and locking mechanism. 2. Inspect sealing gasket (wear, cracks, hardening). 3. Check for material leakage. Replacement - Wear Liners Replacement 1. Remove bolts and dismantle worn liners. 2. Clean and inspect installation surface. 3. Install new liners in correct position. 3. Check alignment and fit-up. 4. Tighten bolts to specified torque. - Flow Driver Replacement 1. Prepare tools, lifting equipment 2. Remove old Flow Driver. 3. Inspect and clean shaft, coupling, and base. 4. Install new unit and perform alignment. 5. Tighten bolts to specified torque. - Bearing Housing Replacement 1. Mark position and remove old bearing housing. 2. Inspect and clean shaft and mounting base. 3. Install new bearing housing. 4. Tighten locking device and bolts to specified torque. 5. Lubricate as required. Final Inspection & Test Run 1. Verify all components are properly installed and secured. 2. Check for leakage, looseness, and abnormal condition. 3. Perform test run (no load → load). 4. Monitor vibration, noise, and operating condition. 5. Confirm stable and normal operation. | Set | 2 |
| 68 | CV 02 CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools. 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 1 |
| 69 | CV 02 CONVEYOR - Gear Box B213HSA-C14+UF21-ZF21892 | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 1 |
| 70 | CV 02 CONVEYOR - Fluid Coupling YOTVNZ - 875 | Inspect Fluid couplings : 1. Check for oil leakage, loose bolts, and casing condition. 2. Check oil level and oil condition. 3. Check vibration and abnormal noise during operation. 4. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Drain all old oil and inspect its condition. 2. Reinstall and tighten the drain plug. 3. Fill with the correct type and level of oil. 4. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Remove the old coupling and inspect the shaft. 2. Install the new coupling and tighten properly. 3. Fill with the correct type and amount of oil. 4. Align and perform a test run. | Set | 1 |
| 71 | CV 02 CONVEYOR - Brake YWZ9-630 - TH III - 3006 | Inspection 1. Check overall condition (cracks, looseness, dirt). 2. Check brake pad wear and condition. 3. Measure and verify brake air gap. 4. Inspect brake disc/drum surface (wear, scoring, damage). 5. Check brake mechanism (spring, rod, movement, jamming). 6. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 7. Perform test run and evaluate braking performance (response, holding capacity). 8. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Prepare tools, spare parts 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 1 |
| 72 | CV 02 CONVEYOR - Gear Coupling TY - SB - 250 | Inspection 1. Prepare tools. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Clean the coupling area and remove the cover. 2. Inspect internal condition of gears and seals. 3. Apply specified grease with correct type and quantity. 4. Reinstall the cover and tighten bolts securely. 5. Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts. 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 1 |
| 73 | CV 03 CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 227m with 5.joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 74 | CV 03 CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 10 |
| 75 | CV 03 CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 20 |
| 76 | CV 03 CONVEYOR - Ilder | Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. | Pack | 1 |
| 77 | CV 03 CONVEYOR - Skirt Rubber and Sealing System | Replace Skirt & Sealing : 1.Prepare materials and tools. 2.Remove the clamp bolts and dismantle the old skirt and sealing. 3.Clean the installation area thoroughly. 4.Install the new skirt in the correct position. 5.Install the new sealing and tighten all bolts securely. | Set | 1 |
| 78 | CV 03 CONVEYOR - Transfer Chutes and Inspection Doors | Inspection: - Transfer Chute 1. Inspect internal wear condition. 2. Check for blockage and material buildup. 3. Inspect for leakage and spillage. 4. Record findings. - Wear Liners: 1. Check wear condition and measure remaining thickness. 2. Inspect for cracks, delamination, and deformation. 3. Check fastening condition (bolts, looseness). 4. Verify liner fit-up, gap, and alignment. - Doors & Sealing 1. Check door operation and locking mechanism. 2. Inspect sealing gasket (wear, cracks, hardening). 3. Check for material leakage. Replacement - Wear Liners Replacement 1. Remove bolts and dismantle worn liners. 2. Clean and inspect installation surface. 3. Install new liners in correct position. 3. Check alignment and fit-up. 4. Tighten bolts to specified torque. - Flow Driver Replacement 1. Prepare tools, lifting equipment 2. Remove old Flow Driver. 3. Inspect and clean shaft, coupling, and base. 4. Install new unit and perform alignment. 5. Tighten bolts to specified torque. - Bearing Housing Replacement 1. Mark position and remove old bearing housing. 2. Inspect and clean shaft and mounting base. 3. Install new bearing housing. 4. Tighten locking device and bolts to specified torque. 5. Lubricate as required. Final Inspection & Test Run 1. Verify all components are properly installed and secured. 2. Check for leakage, looseness, and abnormal condition. 3. Perform test run (no load → load). 4. Monitor vibration, noise, and operating condition. 5. Confirm stable and normal operation. | Set | 2 |
| 79 | CV 03 CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools. 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 1 |
| 80 | CV 03 CONVEYOR - Gear Box B212HSA - C14 + UF21 | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 1 |
| 81 | CV 03 CONVEYOR - Fluid Coupling YOTCS - 750B | Inspect Fluid couplings : 1. Check for oil leakage, loose bolts, and casing condition. 2. Check oil level and oil condition. 3. Check vibration and abnormal noise during operation. 4. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Drain all old oil and inspect its condition. 2. Reinstall and tighten the drain plug. 3. Fill with the correct type and level of oil. 4. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Remove the old coupling and inspect the shaft. 2. Install the new coupling and tighten properly. 3. Fill with the correct type and amount of oil. 4. Align and perform a test run. | Set | 1 |
| 82 | CV 03 CONVEYOR - Brake YWZ9-630 - TH III - 2006 | Inspection 1. Check overall condition (cracks, looseness, dirt). 2. Check brake pad wear and condition. 3. Measure and verify brake air gap. 4. Inspect brake disc/drum surface (wear, scoring, damage). 5. Check brake mechanism (spring, rod, movement, jamming). 6. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 7. Perform test run and evaluate braking performance (response, holding capacity). 8. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Prepare tools, spare parts 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 1 |
| 83 | CV 03 CONVEYOR - Gear Coupling TY - SB - 225 | Inspection 1. Prepare tools. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Clean the coupling area and remove the cover. 2. Inspect internal condition of gears and seals. 3. Apply specified grease with correct type and quantity. 4. Reinstall the cover and tighten bolts securely. 5. Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts. 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 1 |
| 84 | CV-04A/B CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 192m with 1joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 85 | CV-04A/B CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 10 |
| 86 | CV-04A/B CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 20 |
| 87 | CV-04A/B CONVEYOR - Ilder | Dismantle the cover: Dismantling the cover 1.Preparation work: isolate power supply, place warning tags, and prepare tools. 2. Remove bolts/nuts securing the cover. 3. Use lifting equipment if required and carefully remove the cover from its position. 4. Place the cover in a safe location to prevent deformation or damage. Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. Reinstalling the cover: 1.Inspect the condition of the cover and installation area. 2. Position the cover correctly in its original location. 3.Reinstall and tighten all bolts/nuts to the required torque. 4. Check stability and conduct a trial run. | Pack | 1 |
| 88 | CV-04A/B CONVEYOR - Skirt Rubber and Sealing System | Replace Skirt & Sealing : 1.Prepare materials and tools. 2.Remove the clamp bolts and dismantle the old skirt and sealing. 3.Clean the installation area thoroughly. 4.Install the new skirt in the correct position. 5.Install the new sealing and tighten all bolts securely. | Set | 2 |
| 89 | CV-04A/B CONVEYOR - Transfer Chutes and Inspection Doors | Inspection: - Transfer Chute 1. Inspect internal wear condition. 2. Check for blockage and material buildup. 3. Inspect for leakage and spillage. 4. Record findings. - Wear Liners: 1. Check wear condition and measure remaining thickness. 2. Inspect for cracks, delamination, and deformation. 3. Check fastening condition (bolts, looseness). 4. Verify liner fit-up, gap, and alignment. - Doors & Sealing 1. Check door operation and locking mechanism. 2. Inspect sealing gasket (wear, cracks, hardening). 3. Check for material leakage. Replacement - Wear Liners Replacement 1. Remove bolts and dismantle worn liners. 2. Clean and inspect installation surface. 3. Install new liners in correct position. 3. Check alignment and fit-up. 4. Tighten bolts to specified torque. - Flow Driver Replacement 1. Prepare tools, lifting equipment 2. Remove old Flow Driver. 3. Inspect and clean shaft, coupling, and base. 4. Install new unit and perform alignment. 5. Tighten bolts to specified torque. - Bearing Housing Replacement 1. Mark position and remove old bearing housing. 2. Inspect and clean shaft and mounting base. 3. Install new bearing housing. 4. Tighten locking device and bolts to specified torque. 5. Lubricate as required. Final Inspection & Test Run 1. Verify all components are properly installed and secured. 2. Check for leakage, looseness, and abnormal condition. 3. Perform test run (no load → load). 4. Monitor vibration, noise, and operating condition. 5. Confirm stable and normal operation. | Set | 2 |
| 90 | CV-04A/B CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools. 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 2 |
| 91 | CV-04A/B CONVEYOR - Gear Box B209HSC-C14+UF21+UB11+CW | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 2 |
| 92 | CV-04A/B CONVEYOR - Fluid Coupling YOTVNZ - 650 | Inspect Fluid couplings : 1. Check for oil leakage, loose bolts, and casing condition. 2. Check oil level and oil condition. 3. Check vibration and abnormal noise during operation. 4. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Drain all old oil and inspect its condition. 2. Reinstall and tighten the drain plug. 3. Fill with the correct type and level of oil. 4. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Remove the old coupling and inspect the shaft. 2. Install the new coupling and tighten properly. 3. Fill with the correct type and amount of oil. 4. Align and perform a test run. | Set | 2 |
| 93 | CV-04A/B CONVEYOR - Brake YWZ9-500 - TH III - 1306 | Inspection 1. Check overall condition (cracks, looseness, dirt). 2. Check brake pad wear and condition. 3. Measure and verify brake air gap. 4. Inspect brake disc/drum surface (wear, scoring, damage). 5. Check brake mechanism (spring, rod, movement, jamming). 6. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 7. Perform test run and evaluate braking performance (response, holding capacity). 8. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Prepare tools, spare parts 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 2 |
| 94 | CV-04A/B CONVEYOR - Gear Coupling TY - SB - 175 | Inspection 1. Prepare tools. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Clean the coupling area and remove the cover. 2. Inspect internal condition of gears and seals. 3. Apply specified grease with correct type and quantity. 4. Reinstall the cover and tighten bolts securely. 5. Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts. 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 2 |
| 95 | CV-05A/B CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 192m with 1joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 96 | CV-05A/B CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 12 |
| 97 | CV-05A/B CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 24 |
| 98 | CV-05A/B CONVEYOR - Ilder | Dismantle the cover: Dismantling the cover 1.Preparation work: isolate power supply, place warning tags, and prepare tools. 2. Remove bolts/nuts securing the cover. 3. Use lifting equipment if required and carefully remove the cover from its position. 4. Place the cover in a safe location to prevent deformation or damage. Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. Reinstalling the cover: 1.Inspect the condition of the cover and installation area. 2. Position the cover correctly in its original location. 3.Reinstall and tighten all bolts/nuts to the required torque. 4. Check stability and conduct a trial run. | Pack | 1 |
| 99 | CV-05A/B CONVEYOR - Skirt Rubber and Sealing System | Replace Skirt & Sealing : 1.Prepare materials and tools. 2.Remove the clamp bolts and dismantle the old skirt and sealing. 3.Clean the installation area thoroughly. 4.Install the new skirt in the correct position. 5.Install the new sealing and tighten all bolts securely. | Pack | 1 |
| 100 | CV-05A/B CONVEYOR - Transfer Chutes and Inspection Doors | Inspection: - Transfer Chute 1. Inspect internal wear condition. 2. Check for blockage and material buildup. 3. Inspect for leakage and spillage. 4. Record findings. - Wear Liners: 1. Check wear condition and measure remaining thickness. 2. Inspect for cracks, delamination, and deformation. 3. Check fastening condition (bolts, looseness). 4. Verify liner fit-up, gap, and alignment. - Doors & Sealing 1. Check door operation and locking mechanism. 2. Inspect sealing gasket (wear, cracks, hardening). 3. Check for material leakage. Replacement - Wear Liners Replacement 1. Remove bolts and dismantle worn liners. 2. Clean and inspect installation surface. 3. Install new liners in correct position. 3. Check alignment and fit-up. 4. Tighten bolts to specified torque. - Flow Driver Replacement 1. Prepare tools, lifting equipment 2. Remove old Flow Driver. 3. Inspect and clean shaft, coupling, and base. 4. Install new unit and perform alignment. 5. Tighten bolts to specified torque. - Bearing Housing Replacement 1. Mark position and remove old bearing housing. 2. Inspect and clean shaft and mounting base. 3. Install new bearing housing. 4. Tighten locking device and bolts to specified torque. 5. Lubricate as required. Final Inspection & Test Run 1. Verify all components are properly installed and secured. 2. Check for leakage, looseness, and abnormal condition. 3. Perform test run (no load → load). 4. Monitor vibration, noise, and operating condition. 5. Confirm stable and normal operation. | Set | 2 |
| 101 | CV-05A/B CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools. 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 2 |
| 102 | CV-05A/B CONVEYOR - Gear Box B214HSC-C14+UF21+UB11+CCW+ZF21518 | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 2 |
| 103 | CV-05A/B CONVEYOR - Fluid Coupling YOTVNZ - 875 | Inspect Fluid couplings : 1. Check for oil leakage, loose bolts, and casing condition. 2. Check oil level and oil condition. 3. Check vibration and abnormal noise during operation. 4. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Drain all old oil and inspect its condition. 2. Reinstall and tighten the drain plug. 3. Fill with the correct type and level of oil. 4. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Remove the old coupling and inspect the shaft. 2. Install the new coupling and tighten properly. 3. Fill with the correct type and amount of oil. 4. Align and perform a test run. | Set | 2 |
| 104 | CV-05A/B CONVEYOR - Brake YWZ9-630 - TH III - 3006 | Inspection 1. Check overall condition (cracks, looseness, dirt). 2. Check brake pad wear and condition. 3. Measure and verify brake air gap. 4. Inspect brake disc/drum surface (wear, scoring, damage). 5. Check brake mechanism (spring, rod, movement, jamming). 6. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 7. Perform test run and evaluate braking performance (response, holding capacity). 8. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Prepare tools, spare parts 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 2 |
| 105 | CV-05A/B CONVEYOR - Gear Coupling TY - SB - 250 | Inspection 1. Prepare tools. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Clean the coupling area and remove the cover. 2. Inspect internal condition of gears and seals. 3. Apply specified grease with correct type and quantity. 4. Reinstall the cover and tighten bolts securely. 5. Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts. 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 2 |
| 106 | CV-06A/B CONVEYOR - Conveyor Belt | Inspect belt surface for wear, cracks, and cover delamination : 1.Inspect Cleaning: Clean the surface to reveal damages hidden under dust and debris. 2. Inspet Wear Measurement: Check the rubber thickness to ensure it hasn't worn down to the carcass. 3. Inspect Crack Detection: Look for longitudinal or transverse cracks to prevent extensive belt tearing. 4. Delamination Detection: Inspect for blisters or separation between the cover and the core. Inspect belt tracking, belt misalignment, and belt elongation: 1.Tracking: Monitor the belt's path to ensure it consistently runs in the center. 2. Misalignment: Detect early signs of belt edges rubbing against the frame to prevent tearing or wear. 3. Take-up Unit: Check the remaining travel distance of the tensioning system to evaluate elongation. 4. Measurement: Compare the actual belt length with original specifications to determine the elongation rate. 5.Tension: Ensure the belt does not sag or slip on the pulley due to loss of tension. Inspect belt splices (vulcanized or mechanical joints): 1.Cleaning: Clean the splice area to detect even the smallest cracks or glue failures. 2. Gap Inspection: Check for any signs of separation or widening of the splice joint. 3. Delamination: Look for blisters or peeling of the cover rubber from the carcass. Measure belt thickness at high-load areas: 1.Identification: Focus on loading points and sections passing over drive pulleys. 2. Cleaning: Remove all debris and material buildup for an accurate measurement. 3. Tooling: Use calipers or ultrasonic thickness gauges for inspection. 4. Comparison: Compare readings with original specifications to calculate the wear percentage. Replace belt (Replace individual components 192m with 1joints) 1. Preparation & Inspection 2. Stripping & Cutting the Belt Ends 3. Stepping / Stripping the Plies 4. Buffing & Surface Cleaning 5.Cementing & Rubber Lay-up 6. Hot Vulcanization 7.Cooling Down & Quality Inspection 8 Commissioning & Trial Run | Pack | 1 |
| 107 | CV-06A/B CONVEYOR - Pulley (Driver, Tail, Snup, Bend) | - Inspection 1. Inspect wear and damage condition of the rubber lagging. 2. Check for debonding and adhesion condition of the rubber layer. 3. Check pulley run-out, alignment, and bearing condition. 4. Check for belt slippage and abnormal vibration during operation. 5. Evaluate condition and determine need for repair or replacement. - Replacement : 1. Preparation: Prepare new pulley, lifting equipment, and ensure safety (LOTO). 2. Disassembly: Release belt tension, remove bearing housings, and dismantle the old pulley. 3. Inspection: Inspect and clean shaft, bearings, and mounting surfaces. 4. Assembly: Install new bearings and verify lagging groove direction. 5. Installation: Install pulley into frame and align shaft perpendicular to belt centerline. 6. Tracking: Re-tension the belt and adjust tracking. - Final Check & Test Run: 1. Perform test run (no load → load). 2. Check alignment, vibration, noise, and belt tracking. 3. Confirm stable and normal operation. | Set | 22 |
| 108 | CV-06A/B CONVEYOR - Bearing and Bearing house | - Inspection 1. Check bearing internal clearance using feeler gauge or dial indicator. 2. Measure housing temperature using infrared thermometer. 3. Perform acoustic inspection (abnormal noise detection). 4. Check vibration level to detect looseness or misalignment. 5. Inspect lubrication condition: 5.1 Grease level and cleanliness 5.2 Check for contamination (metal particles, burnt smell, hardening) 5.3 Ensure grease nipples are not clogged 6. Verify operating temperature 7. Evaluate condition and determine need for re-greasing or replacement. - Maintenance – Greasing 1. Clean bearing housing and grease nipples. 2. Add specified grease with correct quantity. 3. Remove excess grease and clean surrounding area. 4. Perform short test run and recheck condition. - Replacement: 1. Prepare tools and mark installation position. 2. Remove bolts and dismantle old bearing housing. 3. Inspect and clean shaft and mounting base. 4. Install new bearing housing and locking device. 5. Tighten bolts to specified torque. 6. Lubricate bearing as required. 7. Check alignment and ensure proper installation. - Final Check & Test Run 1. Perform test run 2. Check temperature, vibration, and noise. 3. Inspect for grease leakage or abnormal condition. 4. Confirm stable and normal operation. | Set | 44 |
| 109 | CV-06A/B CONVEYOR - Ilder | Dismantle the cover: Dismantling the cover 1.Preparation work: isolate power supply, place warning tags, and prepare tools. 2. Remove bolts/nuts securing the cover. 3. Use lifting equipment if required and carefully remove the cover from its position. 4. Place the cover in a safe location to prevent deformation or damage. Inspect noise, vibration, and temperature : 1.Observe and listen for abnormal noise during operation. 2. Check vibration by touch or using a vibration measuring device. 3. Measure the roller surface temperature using an infrared thermometer. 4. Evaluate the condition and plan replacement if necessary. Replace Ilder : 1.Preparation work: prepare tools, lifting equipment, and implement safety measures. 2. Lift or secure the conveyor belt to create sufficient clearance. 3. Remove the damaged roller from the frame. 4. Install the new roller in the correct position and check smooth rotation. 5.Lower the belt, conduct a trial run, and inspect operating condition. Reinstalling the cover: 1.Inspect the condition of the cover and installation area. 2. Position the cover correctly in its original location. 3.Reinstall and tighten all bolts/nuts to the required torque. 4. Check stability and conduct a trial run. | Pack | 1 |
| 110 | CV-06A/B CONVEYOR - Counter Weight | Inspect take-up travel and working range: 1.Visual inspection Check the take-up position, guide rails, and overall mechanical condition. 2. Travel inspection Ensure sufficient remaining travel (min–max) and confirm it does not reach mechanical limits. 3. Working range inspection Verify proper belt tension — not over-tensioned or too loose. 4. Safety check & test run Inspect connections and limit switches, then conduct a test run to confirm proper operation. Inspect conveyor belt elongation : 1.Mark two fixed points on the belt at a known distance (e.g., 1–2. m). 2. Measure the distance between the two marks after a period of operation. 3. Compare the measured length with the original length. 4. Calculate the elongation percentage: 5.Evaluate against allowable limits to decide whether tension adjustment or belt replacement is required. Replace travel frame : 1.Preparation Prepare materials, tools. 2. Suspend the counterweight Securely lift and fix the counterweight before removing the frame. 3. Remove the old frame Disconnect all connections and remove the frame from its position. 4. Related inspection Inspect the rails, wheels, and mounting surfaces. 5.Install the new frame Align properly, install, and tighten bolts to the specified standard. 6. Inspection & test run Perform final checks and conduct a test run to confirm stable operation. | Set | 2 |
| 111 | CV-06A/B CONVEYOR - Gear Box B212HSC-C14+UF21+UB11+CCW | 1. Stop equipment, isolate power, apply LOTO. 2. Drain oil, remove gearbox cover, and dismantle gears and bearings. 3. Clean components and inspect gears and bearings for wear, cracks, and damage. 4. Decide repair or full gearbox replacement. 5. Replace damaged gears/bearings or install new gearbox if required. 6. Inspect the rubber element of the hydraulic coupling for wear, cracks, or deformation; replace if damaged. 7. Reassemble components and fill oil to correct specification. 8. Perform alignment between motor, coupling, and gearbox; adjust shims and tighten bolts. 9. Check bolts, oil level, and installation condition. 10. Run no-load first, then monitor noise, vibration, temperature, and leakage. | Set | 2 |
| 112 | CV-06A/B CONVEYOR - Fluid Coupling YOTVNZ - 750 | Inspect Fluid couplings : 1. Check for oil leakage, loose bolts, and casing condition. 2. Check oil level and oil condition. 3. Check vibration and abnormal noise during operation. 4. Verify alignment and adjust if necessary. Replace Fluid Coupling Oil : 1. Drain all old oil and inspect its condition. 2. Reinstall and tighten the drain plug. 3. Fill with the correct type and level of oil. 4. Perform a test run and check for leaks. Replace Fruid Coupling : 1. Remove the old coupling and inspect the shaft. 2. Install the new coupling and tighten properly. 3. Fill with the correct type and amount of oil. 4. Align and perform a test run. | Set | 2 |
| 113 | CV-06A/B CONVEYOR - Brake YWZ9-630 - TH III - 2006 | Inspection 1. Check overall condition (cracks, looseness, dirt). 2. Check brake pad wear and condition. 3. Measure and verify brake air gap. 4. Inspect brake disc/drum surface (wear, scoring, damage). 5. Check brake mechanism (spring, rod, movement, jamming). 6. Check hydraulic/electrical system (oil level, leaks, pressure, wiring). 7. Perform test run and evaluate braking performance (response, holding capacity). 8. Assess condition and determine maintenance or replacement. Maintenance – Brake Oil Replacement 1. Prepare tools, equipment, and specified brake oil. 2. Drain the old brake oil completely. 3. Clean reservoir, pipelines, and system components. 4. Refill with new brake oil to specified level. 5. Bleed air from the system to ensure proper operation. 6. Inspect for leaks and proper pressure. 7. Perform test run and confirm normal brake performance. Replacement – Brake Pads (if required) 1. Prepare tools, spare parts 2. Remove guard and brake assembly. 3. Remove worn brake pads. 4. Clean brake disc and mounting surfaces. 5. Install new brake pads. 6. Adjust brake clearance (air gap) to specification. 7. Tighten all bolts to required torque. 8. Perform test run and verify braking performance. Replacement – Brake Assembly (if required) 1. Prepare tools, spare parts 2. Remove guard and dismantle the old brake. 3. Inspect and clean mounting surface. 4. Install new brake and reconnect wiring/hydraulic lines. 5. Adjust brake air gap to specified value. 6. Perform alignment if required. 7. Conduct test run and verify stable and safe operation. | Set | 2 |
| 114 | CV-06A/B CONVEYOR - Gear Coupling TY - SB - 225 | Inspection 1. Prepare tools. 2. Check bolts, guard, and external condition of the coupling. 3. Inspect lubrication condition and grease level. 4. Inspect gear teeth for wear, pitting, or damage. 5. Check vibration and abnormal noise during operation. 6. Verify alignment and adjust if necessary. 7. Evaluate condition and determine maintenance or replacement. Maintenance – Greasing : 1. Clean the coupling area and remove the cover. 2. Inspect internal condition of gears and seals. 3. Apply specified grease with correct type and quantity. 4. Reinstall the cover and tighten bolts securely. 5. Perform inspection and test run to ensure normal operation. Replacement: 1. Prepare tools, spare parts. 2. Remove guard and dismantle the old coupling. 3. Inspect and clean shaft, key, and mounting surfaces. 4. Install new coupling and tighten bolts properly. 5. Lubricate coupling as required. 6. Perform alignment (alignment check & adjustment). 7. Conduct test run and verify stable operation. | Set | 2 |
| 115 | Screen-01A/01B - Screening Shafts, Screening Mesh. | 1. Clean all shafts, sieve plates, and surrounding areas to remove dust, debris, and material buildup. 2. Inspect shafts and sieve plates for wear, cracks, deformation, holes, or damage. 3. Measure shaft run-out, working clearances between shafts, and check sieve plate gaps/thickness at critical points. 4. Inspect screening discs/fins, sieve plates, supporting frames, bolts, and mounting points for wear, looseness, or damage. 5. Check for abnormal vibration, noise, or blockage affecting screening performance. 6. Assess all inspection results and determine whether repair or replacement is required. 7. Dismantle bearings, remove shafts, and remove worn or damaged sieve plates. 8. Repair shafts by welding and machining if applicable, or replace shafts and sieve plates that exceed allowable limits. 9. Reinstall shafts, bearings, sieve plates, and all related components properly. 10. Perform alignment of shafts, adjust clearances, and ensure proper installation and tension of sieve plates. 11. Check all connections, fasteners, and ensure correct assembly. | Set | 28 |
| 116 | Screen-01A/01B - Bearings | 1. Preparation & Access Remove the screening machine covers and ensure safe access to bearings and related components. 2. Cleaning Remove bearing covers and clean the bearings to eliminate grease, dust, and contaminants. 3. Initial Inspection Inspect bearings for abnormal noise, pitting, and discoloration caused by overheating. 4. Clearance Measurement Check and measure radial and axial clearances to ensure they are within allowable limits. 5. Temperature Check Measure and record bearing operating temperature before overhaul for comparison. 6. Evaluation & Decision Assess the condition of the bearings to determine whether regreasing or replacement is required. 7. Dismantling Secure the screening machine shafts and dismantle the motor and bearing assemblies. 8. Lubrication Replacement Replace all lubricating grease with new grease according to specifications. 9. Bearing Replacement Replace bearings if they are worn, pitted, overheated, or if clearance exceeds allowable limits. 10. Reinstallation Reinstall bearings, motor, and all related components properly. 11. Alignment & Adjustment Perform alignment of the motor and shafts to ensure proper operation. 12. Final Inspection Check all connections, fasteners, and ensure correct installation. 13. Commissioning & Temperature Verification Perform a test run and measure bearing temperature after overhaul to confirm stable operation. | Set | 56 |
| 117 | Screen-01A/01B - Drive System (Reduce and motor) | 1. Preparation & Safety Isolate the power supply, apply LOTO, and ensure safe access to the motor and gearbox. 2. External Cleaning Clean the motor exterior to remove dust, grease, and contaminants. 3. Electrical Inspection Measure the winding insulation resistance using a megger to assess insulation condition. 4. Operational Condition Check Check motor operating temperature, vibration, and abnormal noise during operation. 5. Mechanical Inspection Inspect the motor base, foundation bolts, and mounting condition. 6. Evaluation & Decision Assess the inspection results to determine whether adjustment, repair, or replacement is required. 7. Disconnection & Dismantling Disconnect electrical wiring, drain the gearbox oil completely, and dismantle the geared motor. 8. Installation of New Geared Motor Install the new geared motor and ensure proper positioning. 9. Alignment & Reconnection Perform alignment between motor and driven equipment, reconnect electrical wiring, and tighten all mounting bolts securely. 10. Final Inspection Verify all connections, oil levels, and installation conditions before operation. 11. Commissioning & Test Run | Set | 28 |
| 118 | Crusher-01A/01B - Main Shaft | 1. Clean the supports, bolts, nuts, and installation area to remove dirt and debris. 2. Assess the condition of the equipment and evaluate the severity of any damage. 3. Determine whether the equipment requires repair or full replacement. 4. Remove the damaged or old equipment and clean the installation area. 5. Send the damaged components to the workshop for repair. 6. Reinstall the repaired equipment or install new equipment as required. 7. Check the opening and closing condition and ensure proper operation after installation. 8. Clean the work area and equipment after installation. 9. Conduct a test run and perform final inspection to ensure normal and stable operation. | Set | 2 |
| 119 | Crusher-01A/01B - Bearings | 1. Clean and dismantle the bearing assembly thoroughly. 2. Inspect the bearing condition, checking for wear, pitting, or surface damage. 3. Replace the bearing if it is damaged or excessively worn. 4. Apply proper lubrication and reinstall the bearing correctly. 5. Perform a test run and monitor to ensure normal operation. | Set | 4 |
| 120 | Crusher-01A/01B - Gear Coupling | 1. Clean and dismantle the bearing assembly thoroughly. 2. Inspect the bearing condition, checking for wear, pitting, or surface damage. 3. Replace the gear coupling if it is damaged or excessively worn. 4. Apply proper lubrication and reinstall the bearing correctly. 5. Perform a test run and monitor to ensure normal operation. | Set | 2 |
| 121 | Crusher-01A/01B - Ring hammer | 1. Inspect the ring hammers for wear, cracks, deformation, and uneven thickness. 2. Check for proper installation, looseness, and balance condition. 3. Replace any damaged or excessively worn ring hammers to ensure efficient crushing performance. | Set | 2 |
| 122 | Crusher-01A/01B - Impact plate | 1. Clean the area and dismantle all impact/screen plates. 2. Measure the clearance and gaps according to technical requirements. 3. Perform visual inspection to check for wear, cracks, or damage. 4. Evaluate the condition and determine if replacement is required. 5. Replace all plates if they are worn or damaged. 6. Reinstall the plates and perform proper alignment. 7. Conduct a test run to ensure normal operation. | Set | 2 |
| 123 | Crusher-01A/01B - Sieve plate | 1. Clean the area and dismantle all sieve plates. 2. Measure the clearance and gaps according to technical requirements. 3. Perform visual inspection to check for wear, cracks, or damage. 4. Evaluate the condition and determine if replacement is required. 5. Replace all sieve plates if they are worn or damaged. 6. Reinstall the sieve plates and perform proper alignment. 7. Conduct a test run to ensure normal operation. | Set | 2 |
| 124 | Crusher-01A/01B - Crushing plate | 1. Clean the area and dismantle all impact/screen plates. 2. Measure the clearance and gaps according to technical requirements. 3. Perform visual inspection to check for wear, cracks, or damage. 4. Evaluate the condition and determine if replacement is required. 5. Replace all plates if they are worn or damaged. 6. Reinstall the plates and perform proper alignment. 7. Conduct a test run to ensure normal operation. | Set | 2 |
| 125 | MAGNETIC SEPARATOR 01-04 - Magnet Assembly & Magnet box | 1. Monitor magnetic pull strength, check the magnet box casing for dents or cracks, and clear accumulated tramp iron. If replacement is determined, apply LOTO. 2. Strictly use synthetic slings or non-magnetic rigging. Loosen the turnbuckles or suspension chains, then hoist the old magnet assembly away from the conveyor line. 3. Hoist the new magnet assembly onto the supports. Adjust to the optimal suspension height above the belt to ensure extraction force, secure the anchor points, and throw a metal piece to practically test it. | Set | 5 |
| 126 | MAGNETIC SEPARATOR 01-04 - Gearbox | 1. Monitor for abnormal noise, vibration, casing temperature, check the oil sight glass, and visually inspect shaft seals for leaks during operation. Once replacement is decided, stop the machine and apply LOTO. 2. Drain the old gear oil. Remove safety guards, disconnect the coupling, or remove the belt/chain drive connected to the drive pulley. Remove base bolts and hoist the damaged gearbox off the base plate. 3. Clean the base plate surface, hoist the new gearbox into position. Perform shaft alignment or re-tension the drive belt/chain. Apply standard torque to base bolts, fill with new gear oil to the correct level, and perform a test run. | Set | 5 |
| 127 | MAGNETIC SEPARATOR 01-04 - Rollers | 1. Check for binding or shell wear. Stop the machine and apply LOTO. 2. Fully loosen the take-up to completely slacken the belt. 3. Unbolt both pillow blocks and use soft slings to hoist the old roller out. 4. Hoist the new roller into the belt, square the shaft, and tighten base bolts. 5. Re-tension the belt, remove LOTO, test run, and adjust tracking if needed. | Set | 10 |
| 128 | MAGNETIC SEPARATOR 01-04 - Bearings | 1. Check for noise or heat. Stop the machine and apply LOTO. 2. Loosen the take-up to release belt tension on the shaft. 3. Remove base bolts, loosen set screws, and use a puller to extract the old bearing. 4. Clean the shaft journal, install the new bearing, torque bolts, and lock set screws. 5. Pump grease, re-tension the belt, and perform a no-load test run. | Set | 20 |
| 129 | MAGNETIC SEPARATOR 01-04 - Belt | 1. Check cleats for wear or cracks. Stop the machine and apply LOTO. 2. Fully loosen the take-up unit bolts to maximize belt slack. 3. Remove the mechanical splice pin or cut the old belt to extract it. 4. Thread the new belt around the pulleys. Pull the ends together and insert the splice pin. 5. Evenly tighten both sides of the take-up. Remove LOTO, test run, and adjust tracking until centered. | Set | 5 |
| 130 | MAGNETIC SEPARATOR 01-04 - Dust shield | 1. Locate tears or coal dust leaks. Stop the machine and apply LOTO. 2. Remove bolts and take off the retaining strips holding the shield. 3. Pull off the damaged rubber/canvas shield and clean rust/dirt from the frame. 4. Cut the new shield, position it to seal the gap, and tighten the retaining clamps. 5. Verify the seal around the edges, remove LOTO, and test run to confirm zero dust emission. | Set | 5 |
| 131 | Dust Collector System-01 - Exhaust fan | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 4 |
|  |  | Bearing housing 1. Clean and dismantle the bearing housing thoroughly. 2. Inspect the housing condition, checking for wear, cracks, deformation, or corrosion. 3. Check the housing seat and mounting surfaces for damage or looseness. 4. Repair or replace the housing if defects exceed allowable limits. 5. Reinstall the housing and perform a test run to ensure proper operation. | Set | 1 |
|  |  | Bearing 1. Clean and dismantle the bearing assembly thoroughly. 2. Inspect the bearing condition, checking for wear, pitting, or surface damage. 3. Replace the bearing if it is damaged or excessively worn. 4. Apply proper lubrication and reinstall the bearing correctly. 5. Perform a test run and monitor to ensure normal operation. | Set | 2 |
|  |  | Fan 1. Clean the impeller to remove dust, dirt, and material buildup. 2. Check for wear, cracks, corrosion, or deformation of the blades. 3. Inspect for imbalance, misalignment, or uneven wear. 4. Check bolts, hub, and connections for looseness or damage. 5. Monitor vibration and abnormal noise during operation. 6. Repair, rebalance, or replace the impeller if defects are found. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 132 | Dust Collector System-01 - Hopper and auxiliary piping. | Visual inspection 1. Check for leakage 2. Remove rust and repaint corroded areas 3. Tighten loose bolts | Set | 1 |
|  |  | Filter bag 1. LOTO DCS-01 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-01 | Set | 196 |
|  |  | Hopper 1. LOTO DCS-01 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-01 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-01 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 4. Remove LOTO from DCS-01 | Set | 2 |
| 133 | Dust Collector System-01 - Screw conveyor shaft | Visual inspection 1. Check for leakage 2. Clean coal buildup on the inner pipe wall 3. Remove slag and repaint corroded areas | Set | 3 |
|  |  | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 6 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 3 |
| 134 | Dust Collector System-01 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 2 |
|  |  | Air filter 1. LOTO the air compressor 2. Remove the old filter, clean it or replace it with a new one 3. Remove LOTO | Set | 1 |
| 135 | Dust Collector System-02 - Exhaust fan | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 4 |
|  |  | Bearing housing 1. Clean and dismantle the bearing housing thoroughly. 2. Inspect the housing condition, checking for wear, cracks, deformation, or corrosion. 3. Check the housing seat and mounting surfaces for damage or looseness. 4. Repair or replace the housing if defects exceed allowable limits. 5. Reinstall the housing and perform a test run to ensure proper operation. | Set | 1 |
|  |  | Bearing 1. Clean and dismantle the bearing assembly thoroughly. 2. Inspect the bearing condition, checking for wear, pitting, or surface damage. 3. Replace the bearing if it is damaged or excessively worn. 4. Apply proper lubrication and reinstall the bearing correctly. 5. Perform a test run and monitor to ensure normal operation. | Set | 2 |
|  |  | Fan 1. Clean the impeller to remove dust, dirt, and material buildup. 2. Check for wear, cracks, corrosion, or deformation of the blades. 3. Inspect for imbalance, misalignment, or uneven wear. 4. Check bolts, hub, and connections for looseness or damage. 5. Monitor vibration and abnormal noise during operation. 6. Repair, rebalance, or replace the impeller if defects are found. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 136 | Dust Collector System-02 - Hopper and auxiliary piping. | Visual inspection 1. Check for leakage 2. Remove rust and repaint corroded areas 3. Tighten loose bolts | Set | 1 |
|  |  | Filter bag 1. LOTO DCS-02 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-02 | Set | 196 |
|  |  | Hopper 1. LOTO DCS-02 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-02 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-02 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from DCS-02 | Set | 2 |
| 137 | Dust Collector System-02 - Screw conveyor shaft | Visual inspection 1. Check for leakage 2. Clean coal buildup on the inner pipe wall 3. Remove slag and repaint corroded areas | Set | 3 |
|  |  | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 6 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 3 |
| 138 | Dust Collector System-02 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 2 |
|  |  | Air filter 1. LOTO the air compressor 2. Remove the old filter, clean it or replace it with a new one 3. Remove LOTO | Set | 1 |
| 139 | Dust Collector System-03 - Exhaust fan | Visual inspection 1. Clean the equipment 2. Check oil level 3. Remove rust and repaint corroded areas 4. Perform a test run to check vibration and noise | Set | 1 |
|  |  | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 4 |
|  |  | Bearing housing 1. Clean and dismantle the bearing housing thoroughly. 2. Inspect the housing condition, checking for wear, cracks, deformation, or corrosion. 3. Check the housing seat and mounting surfaces for damage or looseness. 4. Repair or replace the housing if defects exceed allowable limits. 5. Reinstall the housing and perform a test run to ensure proper operation. | Set | 1 |
|  |  | Bearing 1. Clean and dismantle the bearing assembly thoroughly. 2. Inspect the bearing condition, checking for wear, pitting, or surface damage. 3. Replace the bearing if it is damaged or excessively worn. 4. Apply proper lubrication and reinstall the bearing correctly. 5. Perform a test run and monitor to ensure normal operation. | Set | 2 |
|  |  | Fan 1. Clean the impeller to remove dust, dirt, and material buildup. 2. Check for wear, cracks, corrosion, or deformation of the blades. 3. Inspect for imbalance, misalignment, or uneven wear. 4. Check bolts, hub, and connections for looseness or damage. 5. Monitor vibration and abnormal noise during operation. 6. Repair, rebalance, or replace the impeller if defects are found. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 140 | Dust Collector System-03 - Hopper and auxiliary piping. | Visual inspection 1. Check for leakage 2. Remove rust and repaint corroded areas 3. Tighten loose bolts | Set | 1 |
|  |  | Filter bag 1. LOTO DCS-03 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-03 | Set | 196 |
|  |  | Hopper 1. LOTO DCS-03 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-03 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-03 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from DCS-03 | Set | 2 |
| 141 | Dust Collector System-03 - Screw conveyor shaft | Visual inspection 1. Check for leakage 2. Clean coal buildup on the inner pipe wall 3. Remove slag and repaint corroded areas | Set | 1 |
|  |  | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 2 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 1 |
| 142 | Dust Collector System-03 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 2 |
|  |  | Air filter 1. LOTO the air compressor 2. Remove the old filter, clean it or replace it with a new one 3. Remove LOTO | Set | 1 |
| 143 | Dust Collector System-04 - Exhaust fan | Fan 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 144 | Dust Collector System-04 - Hopper and auxiliary piping | Filter bag 1. LOTO DCS-04 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-04 | Set | 81 |
|  |  | Hopper 1. LOTO DCS-04 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-04 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-04 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from DCS-04 | Set | 2 |
| 145 | Dust Collector System-04 - Screw conveyor shaft | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 2 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 1 |
| 146 | Dust Collector System-04 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 2 |
|  |  | Air filter 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
| 147 | Dust Collector System-05 - Exhaust fan | Fan 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
| 148 | Dust Collector System-05 - Hopper and auxiliary piping | Filter bag 1. LOTO DCS-05 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-05 | Set | 30 |
|  |  | Hopper 1. LOTO DCS-05 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-05 | Set | 1 |
| 149 | Dust Collector System-06 - Exhaust fan | Fan 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
| 150 | Dust Collector System-06 - Hopper and auxiliary piping. | Filter bag 1. LOTO DCS-06 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-06 | Set | 30 |
|  |  | Hopper 1. LOTO DCS-06 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-06 | Set | 1 |
| 151 | Dust Collector System-07 - Exhaust fan | Fan 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 152 | Dust Collector System-07 - Hopper and auxiliary piping. | Filter bag 1. LOTO DCS-07 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-07 | Set | 72 |
|  |  | Hopper 1. LOTO DCS-07 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-07 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-07 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from DCS-07 | Set | 2 |
| 153 | Dust Collector System-07 - Screw conveyor shaft | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 2 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 1 |
| 154 | Dust Collector System-07 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 2 |
|  |  | Air filter 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
| 155 | Dust Collector System-08 - Exhaust fan | Fan 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
|  |  | Flexible pipe 1. LOTO the fan 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from the fan | Set | 2 |
| 156 | Dust Collector System-08 - Hopper and auxiliary piping | Filter bag 1. LOTO DCS-08 2. Remove the hopper manhole and filter cover 3. Remove the old filter and install a new one 4. Clean the hopper and close the manhole cover 5. Remove LOTO from DCS-07 | Set | 72 |
|  |  | Hopper 1. LOTO DCS-08 2. Clean the equipment, remove rust and repaint corroded areas, and fix leaks 3. Replace the damaged sealing gasket with a new one 4. Remove LOTO from DCS-07 | Set | 1 |
|  |  | Flexible pipe 1. LOTO DCS-08 2. Remove the flexible couplings at the suction and discharge ends and replace them with new ones 3. Remove LOTO from DCS-08 | Set | 2 |
| 157 | Dust Collector System-08 - Screw conveyor shaft | Bearing 1. LOTO the screw conveyor 2. Remove the motor and gearbox 3. Remove the bearing housing 4. Remove the old bearing and install a new bearing 5. Reassemble all components completely 6. Remove LOTO, perform a test run, and inspect | Set | 2 |
|  |  | Reducer 1. Clean the reducer surface to remove oil, dust, and contaminants. 2. Check oil level, leakage, and oil condition (color, contamination). 3. Check temperature, vibration, and abnormal noise during operation. 4. Inspect housing, seals, bolts, and mounting condition. 5. Determine whether repair, oil change, or replacement is required. 6. Replacement (if required) 7. Disconnect coupling, drain oil, and remove the old reducer. 8. Install the new reducer and ensure correct positioning. 9. Align with motor and driven equipment, reconnect coupling, and tighten bolts. 10. Fill with specified lubricant to the correct level. | Set | 1 |
| 158 | Dust Collector System-08 - Air compressor | Screw element 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 1 |
|  |  | Belt 1. Stop the compressor, isolate power, release pressure, and apply LOTO. 2. Clean the compressor and screw element area. 3. Check oil level, oil quality, and contamination (water, dirt, metal particles). 4. Check for oil leakage at seals and connections. 5. Check pressure and airflow to evaluate compressor efficiency. 7. Inspect screw rotors for wear, scoring, or damage. 8. Check bearings and seals for wear, looseness, or overheating signs. 9. Determine whether maintenance, overhaul, or replacement is required. | Set | 2 |
|  |  | Air filter 1. Stop the equipment, isolate power, and apply LOTO, Remover cover. 2. Inspect the belt for wear, cracks, fraying, looseness, or misalignment. 3. Check belt tension and alignment condition. 4. Determine if adjustment or replacement is required. 5. Loosen the motor base and remove the old belt. 6. Install the new belt and ensure correct positioning. 7. Adjust pulley alignment and set proper belt tension. 8. Check all bolts, guards, and installation condition. 9. Start the system and monitor for vibration, noise, and stable operation. | Set | 1 |
| 159 | Sampling System 1800/1400 - Sweep Sampler 1800 S70-1800-450-00A | Serpentine Spring Coupling 1. Perform LOTO procedures, remove the coupling cover, and thoroughly clean out the old grease. 2. Inspect the spring grid for damage and check shaft alignment to determine if replacement is necessary. 3. If in good condition: Pack the spring grid with specialized coupling grease. 4. If replacement is required: Extract the old spring grid and clean the gear teeth. Re-align the shafts and gently tap the new spring grid into place before packing with specialized grease. 5. Secure the cover, tighten the bolts to the specified torque, and perform a test run. | Set | 1 |
|  |  | Plummer Block Housings 1. Perform LOTO procedures. Open the housing cover and inspect the bearing for wear or pitting to determine if replacement is necessary. 2. If in good condition: Thoroughly clean out the old grease, apply the specified amount of new lubricant, reinstall the housing cover, and torque the bolts to specification. 3. If replacement is required: Safely support the shaft, remove the old housing base and bearing, then clean the shaft thoroughly. 4. Install the new bearing and housing, and set the proper internal bearing clearance. 5. Apply the specified grease, torque the base and cover bolts to specification, and perform a test run. | Set | 2 |
| 160 | Sampling System 1800/1400 - Bucket Elevator TL160L | Elevator Belt 1. Apply LOTO procedures and thoroughly clean the component surfaces. 2. Visually inspect or use measuring tools to detect cracks, deformation, and surface expansion. Record damage severity to determine if repairs, restorative welding, or replacement are required. 3. If replacement is necessary: Release the tensioner, remove the buckets, and extract the old belt. 4. Feed the new belt into the system, splice the ends (using vulcanization or mechanical fasteners), and reinstall the buckets. 5. Re-tension the belt, adjust tracking, and perform a no-load test run. | Set | 1 |
| 161 | Sampling System 1800/1400 - Primary Belt Feeder SF1-650 | Annular Flat Belt 1. Perform LOTO procedures and clean component surfaces periodically. 2. Measure and visually inspect the belt for cracks or surface expansion, recording damage severity to determine if replacement is required. 3. For replacement, release tension, remove the old flat belt, and thoroughly clean the pulleys. 4. Carefully slip the new endless belt over the pulleys. Reassemble all bearing housings and torque frame bolts. 5. Adjust the take-up to standard tension. Jog the motor to track the pulleys, ensuring the belt runs centered without rubbing the side frames. 6. Reinstall guards, remove LOTO. Test run on load and monitor the belt tracking trajectory. | Set | 1 |
|  |  | End Cleaning Device 1. Stop the secondary belt feeder, completely isolate power, and apply LOTO. 2. Assess the wear of tungsten blades and check if the spring tensioner is jammed by coal dust. 3. Release all spring tension. Remove locking pins or bolts and slide the blade cartridge off the shaft. 4. Install the new blade cartridge. Align the contact angle and adjust the spring to apply standard pressure against the belt (do not over-tension to prevent belt damage). 5. Clear accumulated coal slag on the brackets. Remove LOTO, test run the belt on load, and visually observe the cleaning efficiency. | Set | 1 |
| 162 | Sampling System 1800/1400 - Crusher MM3U-00 | V-Belt 1. Stop the crusher, isolate motor power, and apply LOTO. Remove the belt drive guard. 2. Check for belt slack, bottom cracking, and side wear. Assess the wear of pulley grooves. 3. Loosen motor base bolts to reduce center distance. Remove all old V-belts from the grooves (do not pry). 4. Install new belts. Crucial note: Always replace as a matched set, never mix old and new belts. 5. Move motor back to tension belts. Use a tension meter and laser to align the pulleys. Install guard, remove LOTO, and test run. | Set | 4 |
|  |  | Plummer Block Housings 1. Perform LOTO procedures. Open the housing cover and inspect the bearing for wear or pitting to determine if replacement is necessary. 2. If in good condition: Thoroughly clean out the old grease, apply the specified amount of new lubricant, reinstall the housing cover, and torque the bolts to specification. 3. If replacement is required: Safely support the shaft, remove the old housing base and bearing, then clean the shaft thoroughly. 4. Install the new bearing and housing, and set the proper internal bearing clearance. 5. Apply the specified grease, torque the base and cover bolts to specification, and perform a test run. | Set | 2 |
| 163 | Sampling System 1800/1400 - Tertiary Belt Feeder SF2-Q350L-A00 | Annular Flat Belt 1. Perform LOTO procedures and clean component surfaces periodically. 2. Measure and visually inspect the belt for cracks or surface expansion, recording damage severity to determine if replacement is required. 3. For replacement, release tension, remove the old flat belt, and thoroughly clean the pulleys. 4. Carefully slip the new endless belt over the pulleys. Reassemble all bearing housings and torque frame bolts. 5. Adjust the take-up to standard tension. Jog the motor to track the pulleys, ensuring the belt runs centered without rubbing the side frames. 6. Reinstall guards, remove LOTO. Test run on load and monitor the belt tracking trajectory. | Set | 1 |
|  |  | End Cleaning Device 1. Stop the secondary belt feeder, completely isolate power, and apply LOTO. 2. Assess the wear of tungsten blades and check if the spring tensioner is jammed by coal dust. 3. Release all spring tension. Remove locking pins or bolts and slide the blade cartridge off the shaft. 4. Install the new blade cartridge. Align the contact angle and adjust the spring to apply standard pressure against the belt (do not over-tension to prevent belt damage). 5. Clear accumulated coal slag on the brackets. Remove LOTO, test run the belt on load, and visually observe the cleaning efficiency. | Set | 1 |
| 164 | Sampling System 1800/1400 - Crusher Model 1824 SRC1824-00 | V-Belt 1. Stop the crusher, isolate motor power, and apply LOTO. Remove the belt drive guard. 2. Check for belt slack, bottom cracking, and side wear. Assess the wear of pulley grooves. 3. Loosen motor base bolts to reduce center distance. Remove all old V-belts from the grooves (do not pry). 4. Install new belts. Crucial note: Always replace as a matched set, never mix old and new belts. 5. Move motor back to tension belts. Use a tension meter and laser to align the pulleys. Install guard, remove LOTO, and test run. | Set | 4 |
|  |  | Plummer Block Housings 1. Perform LOTO procedures. Open the housing cover and inspect the bearing for wear or pitting to determine if replacement is necessary. 2. If in good condition: Thoroughly clean out the old grease, apply the specified amount of new lubricant, reinstall the housing cover, and torque the bolts to specification. 3. If replacement is required: Safely support the shaft, remove the old housing base and bearing, then clean the shaft thoroughly. 4. Install the new bearing and housing, and set the proper internal bearing clearance. 5. Apply the specified grease, torque the base and cover bolts to specification, and perform a test run. | Set | 2 |
| 165 | Sampling System 1800/1400 - Secondary Belt Feeder SF2-450-00 | Annular Flat Belt 1. Perform LOTO procedures and clean component surfaces periodically. 2. Measure and visually inspect the belt for cracks or surface expansion, recording damage severity to determine if replacement is required. 3. For replacement, release tension, remove the old flat belt, and thoroughly clean the pulleys. 4. Carefully slip the new endless belt over the pulleys. Reassemble all bearing housings and torque frame bolts. 5. Adjust the take-up to standard tension. Jog the motor to track the pulleys, ensuring the belt runs centered without rubbing the side frames. 6. Reinstall guards, remove LOTO. Test run on load and monitor the belt tracking trajectory. | Set | 1 |
|  |  | End Cleaning Device 1. Stop the secondary belt feeder, completely isolate power, and apply LOTO. 2. Assess the wear of tungsten blades and check if the spring tensioner is jammed by coal dust. 3. Release all spring tension. Remove locking pins or bolts and slide the blade cartridge off the shaft. 4. Install the new blade cartridge. Align the contact angle and adjust the spring to apply standard pressure against the belt (do not over-tension to prevent belt damage). 5. Clear accumulated coal slag on the brackets. Remove LOTO, test run the belt on load, and visually observe the cleaning efficiency. | Set | 1 |
| 166 | Sampling System 1800/1400 - Sweep Sampler 1400 S70-1400L-00 | Serpentine Spring Coupling 1. Perform LOTO procedures, remove the coupling cover, and thoroughly clean out the old grease. 2. Inspect the spring grid for damage and check shaft alignment to determine if replacement is necessary. 3. If in good condition: Pack the spring grid with specialized coupling grease. 4. If replacement is required: Extract the old spring grid and clean the gear teeth. Re-align the shafts and gently tap the new spring grid into place before packing with specialized grease. 5. Secure the cover, tighten the bolts to the specified torque, and perform a test run. | Set | 2 |
|  |  | Bearing P217 1. Perform LOTO procedures and remove safety guards. Thoroughly clean out the old grease from the housing. 2. Inspect the bearing surfaces for clearance, wear, or pitting to determine if replacement is necessary. 3. If in good condition: Apply the specified type and amount of new grease, then reassemble. 4. If replacement is required: Use a dedicated puller or induction heater to extract the old bearing. Clean the shaft, heat the new bearing if needed, and press it into the correct position. 5. Apply the specified grease, reassemble the housing, and perform a test run. | Set | 4 |
| 167 | Sampling System 1800/1400 - Bucket Elevator TL140L | Elevator Belt 1. Apply LOTO procedures and thoroughly clean the component surfaces. 2. Visually inspect or use measuring tools to detect cracks, deformation, and surface expansion. Record damage severity to determine if repairs, restorative welding, or replacement are required. 3. If replacement is necessary: Release the tensioner, remove the buckets, and extract the old belt. 4. Feed the new belt into the system, splice the ends (using vulcanization or mechanical fasteners), and reinstall the buckets. 5. Re-tension the belt, adjust tracking, and perform a no-load test run. | Set | 2 |
| 168 | Sampling System 1800/1400 - Primary Belt Feeder SF1-Q450 | Annular Flat Belt 1. Perform LOTO procedures and clean component surfaces periodically. 2. Measure and visually inspect the belt for cracks or surface expansion, recording damage severity to determine if replacement is required. 3. For replacement, release tension, remove the old flat belt, and thoroughly clean the pulleys. 4. Carefully slip the new endless belt over the pulleys. Reassemble all bearing housings and torque frame bolts. 5. Adjust the take-up to standard tension. Jog the motor to track the pulleys, ensuring the belt runs centered without rubbing the side frames. 6. Reinstall guards, remove LOTO. Test run on load and monitor the belt tracking trajectory. | Set | 2 |
|  |  | End Cleaning Device 1. Stop the secondary belt feeder, completely isolate power, and apply LOTO. 2. Assess the wear of tungsten blades and check if the spring tensioner is jammed by coal dust. 3. Release all spring tension. Remove locking pins or bolts and slide the blade cartridge off the shaft. 4. Install the new blade cartridge. Align the contact angle and adjust the spring to apply standard pressure against the belt (do not over-tension to prevent belt damage). 5. Clear accumulated coal slag on the brackets. Remove LOTO, test run the belt on load, and visually observe the cleaning efficiency. | Set | 2 |
| 169 | Sampling System 1800/1400 - Crusher MM3-00B | V-Belt 1. Stop the crusher, isolate motor power, and apply LOTO. Remove the belt drive guard. 2. Check for belt slack, bottom cracking, and side wear. Assess the wear of pulley grooves. 3. Loosen motor base bolts to reduce center distance. Remove all old V-belts from the grooves (do not pry). 4. Install new belts. Crucial note: Always replace as a matched set, never mix old and new belts. 5. Move motor back to tension belts. Use a tension meter and laser to align the pulleys. Install guard, remove LOTO, and test run. | Set | 8 |
|  |  | Plummer Block Housings 1. Perform LOTO procedures. Open the housing cover and inspect the bearing for wear or pitting to determine if replacement is necessary. 2. If in good condition: Thoroughly clean out the old grease, apply the specified amount of new lubricant, reinstall the housing cover, and torque the bolts to specification. 3. If replacement is required: Safely support the shaft, remove the old housing base and bearing, then clean the shaft thoroughly. 4. Install the new bearing and housing, and set the proper internal bearing clearance. 5. Apply the specified grease, torque the base and cover bolts to specification, and perform a test run. | Set | 4 |
| 170 | Sampling System 1800/1400 - Secondary Belt Feeder SF2-Q350L | Annular Flat Belt 1. Perform LOTO procedures and clean component surfaces periodically. 2. Measure and visually inspect the belt for cracks or surface expansion, recording damage severity to determine if replacement is required. 3. For replacement, release tension, remove the old flat belt, and thoroughly clean the pulleys. 4. Carefully slip the new endless belt over the pulleys. Reassemble all bearing housings and torque frame bolts. 5. Adjust the take-up to standard tension. Jog the motor to track the pulleys, ensuring the belt runs centered without rubbing the side frames. 6. Reinstall guards, remove LOTO. Test run on load and monitor the belt tracking trajectory. | Set | 2 |
|  |  | End Cleaning Device 1. Stop the secondary belt feeder, completely isolate power, and apply LOTO. 2. Assess the wear of tungsten blades and check if the spring tensioner is jammed by coal dust. 3. Release all spring tension. Remove locking pins or bolts and slide the blade cartridge off the shaft. 4. Install the new blade cartridge. Align the contact angle and adjust the spring to apply standard pressure against the belt (do not over-tension to prevent belt damage). 5. Clear accumulated coal slag on the brackets. Remove LOTO, test run the belt on load, and visually observe the cleaning efficiency. | Set | 2 |
| 171 | Pull cord switch | Inspect the junction box and pull cord switch 1 Work Procedure 1.1 General 1.1.1 Cable entries, cable glands, blanking plugs, must be checked for correct tightness. 1.1.2 Check the power supply, wire connections, connector & extension probe connectors and tighten them, contact cleaner or any other available carbon removal aid if connections found rusty & carbonized, if necessary, replaced them conditionally. 1.1.3 Clean the relative accessories like local field junction boxes with brush & waste cotton, or any similar cleaning aid item available. 1.1.4 Check supply voltages. 1.2 Pull Switch Maintenance 1 Make sure the belt is in a steady state. 2 Arrange to get access to junction box. 3 Remove power supply & feedback signal cables from local junction boxes and provide insulation to cables using proper insulated tools. 4 Remove cables and use proper screwdriver & provide insulation for cables. 5 Make sure Micro Switches do not damage & looseness of cable. 6 Check hardness of cable. 7 Clean Micro Switches use waste cotton. 8 Use contact cleaner to clean & decrease connector of Micro Switches & extension cable. 9 Make sure there is a cable shortage along with ground & connector. 10 Make sure Cable gland is properly adjusted after reinstating cables. 11 Pull Switch is an Emergency stop Switch to stop the conveyor belt instantly when an accident happens. Since the Pull Switch is designed that it should be installed at the side of conveyor belt and the Pull Switch should be mounted along conveyor, the switch can be actuated at any position. 12 Make sure physical appearance of Pull code Switch/Chute Plug & clean it with degreaser or waste cotton. | Pack | 1 |
| 172 | Belt sway switch | Inspect the junction box and belt sway switch 1.1 Make sure the belt is in a steady state. 1.2 Arrange to get access to junction box. 1.3 Remove power supply & feedback signal cables from local junction boxes and provide Insulation to cables using proper insulated tools. 1.4 Remove cables and use proper screwdriver & provide insulation to cables. 1.5 Make sure Micro Switches do not damage & looseness of cable. 1.6 Check hardness of cable. 1.7 Clean Micro Switches use waste cotton. 1.8 Use contact cleaner to clean & decrease connector of Micro Switches & extension cable. 1.9 Make sure there is a cable shortage along with ground & connector. 1.10 Make sure Cable gland is properly adjusted after reinstating cables. 1.11 The belt sway Switch allows smooth running of the conveyor and protects it from damages by over swaying which can occur due to uneven loading of material, worn out idle roller bearings. 1.12 Make sure physical appearance of belt sway Switch & clean it with degreaser or waste cotton. | Pack | 1 |
| 173 | Warning horn | Inspect and clean the junction box, siren, and replace any oxidized JB, siren 1. External Inspection (Mechanical) - Inspect the siren body and beacon cover for cracks or deformation. - Check for corrosion, water ingress, or dust accumulation. - Ensure mounting brackets and bolts are secure. - Inspect cable glands, power cables, and junction box condition. 2. Disassembly & Cleaning - Remove the siren cover / beacon dome. - Clean the internal components: - Dust and dirt - Insects - Moisture 3. Electrical Inspection - Verify the power supply rating (AC/DC) - Measure the resistance of the siren coil / circuit. - Inspect terminals and cable lugs: - No burning or oxidation - Tight and secure connections - Check wiring to the beacon light. 4. Component Inspection & Replacement - Check the siren sound output: - Weak or distorted sound → consider replacement - Check the beacon light: - No light or abnormal flashing → replace lamp or LED module - Replace: - Burnt or oxidized terminal blocks - Damaged or hardened sealing gaskets 5. Reassembly & Mechanical Check - Reassemble all components in the correct order. - Tighten bolts to the specified torque. - Ensure proper sealing for dust and water protection. 6. Functional Test - Restore the power supply. - Perform local test: - Siren sound is clear and loud - Beacon light operates correctly - Test control signal: - From PLC / SCADA / relay - Ensure the siren and beacon operate simultaneously. 7. Completion - Close and seal the siren housing and junction box. - Clean up the work area. | Pack | 1 |
| 174 | Chute block switch | 1. Mechanical inspection: - Check that the sensor is not bent or deformed; ensure bolts and mounting brackets are properly tightened. 2. Electrical inspection: - Check cables, terminals, and junction box; inspect contact operation and measure resistance. 3. Calibration: - Preparation: One bucket of coal; remove the level switch from its mounting position. - Zero point: Set the sensor to the no-load condition and verify the simulated signal. - Span point: Place the sensor in the loaded condition and check sensitivity (response time in seconds); adjust the activation time; verify the signal transmitted to SCADA; remove the sensor head and confirm the no-load signal is restored. 4. Cleaning: - Clean the sensor head and the junction box. 5. Reinstallation and final check: - Reinstall the device and verify that the signal is operating normally. | Pack | 1 |
| 175 | Under speed SW | 1 Make sure machines are in a steady state, at zero RPM and LOTO shell applied to system. 2 Arrange to get access to probe via removing gear box casing & if applicable. 3 Measure Gap by filler gauge and it should be 0.8 to 1.5 mm or recommended by OEM. 4 Count the upper side thread of probe and mark it and note down. 5 Remove power supply & feedback signal cables from local junction boxes or Tachometer and provide insulation to cables using proper insulated tools. 6 Remove cables from Junction box or Tachometer using proper screwdriver & provide insulation to cables. 7 Unscrew probe from its mounting support. 8 Release cables from cable buckles/catchers provided inside turbine bearing housing. 9 Disconnect probe, & extension cables via loosing connector, rotate it anti clockwise. 10 Measure probe resistance via using multi meter to ensure its integrity should be within limit of as per OEM manual. 11 Make sure probe tip is not damage & looseness of cable. 12 Check hardness of probe cable & observe seepage oil in cable insulation. 13 Clean oil from probe via using digresser & use waste cotton. 14 Use contact cleaner to clean & decrease connector of sensor & extension cable. 15 Make sure there is a cable shortage along with ground & connector. 16 Reinstate the whole system after completion of the system integrity level test. 17 Make sure oil sealing is properly adjusted after reinstatement of probes. 18 Properly adjusted after reinstatement of probes. | Pack | 1 |
| 176 | Pressure transmitter / differential pressure transmitter | 9 Work Procedure 1.1 General 1.1.1 Inspect the instrument's pressure connection, cable gland etc. Check the wire connections inside & tighten them, if necessary. 1.1.2 Clean the instrument with brush & waste cotton, or any similar cleaning aid item available. Note: Low pressure air may be used for internal cleaning. 1.2 Removal of Instrument 1 Obtain Permit to Work from Operation. 2 Locate the transmitter in field and verifies that this transmitter has same KKS no written-on work permit. After verification slowly close its high-pressure and low-pressure isolation valves simultaneously. 3 Open the equalizing valve in the Transmitter manifold. 4 Open the vent valve slowly and depressurize the Transmitter 5 Neatly note down the wire colors & cable marker numbers along with TB and screw numbers. Remove the cables connected to the transmitter one by one and put insulation tape. If onsite calibration is not possible, dismantle and remove the transmitter from location 6 Clean the transmitter body and process connections. Connect transmitter to the Pressure Calibrator. Connect to the High-pressure port and keep the low-pressure port open to atmosphere. Connect the precision Digital Multi meter to the transmitter through the desktop power supply of 24 Volts DC and a series resistor of 250 ohms. Select 0-100 mA range in the multi meter. Connect the Hart Communicator to the transmitter terminals. 7 Apply 0%, 25%, 50%, 75% and 100% of the range of transmitter under test using the Calibrator and note down the as found mA readings in the calibration sheet. 8 Adjust Zero in the transmitter if necessary, using the Hart Communicator. Refer Hart Communicator manual for operating instructions. 9 Apply full-scale pressure to the transmitter under test and adjust the span to read full scale using the Hart Communicator 10 Repeat steps (6) and (7) till zero and span are set correctly. In case unable to set correctly, reject the instrument. 11 Apply 0%, 25%, 50%, 75% and 100% of the range of transmitter under test using the pressure Calibrator for both increasing and decreasing sequence and note down the as left readings in the calibration sheet. 12 If the transmitter is beyond acceptable limits notify to immediate supervisor. Refer instruction for acceptable limits for various instruments. 13 Put calibration sticker on the transmitter with details as per instruction for calibrated instruments tagging and record keeping. 14 Remove the transmitter under test from the pressure calibrator and install at site and checked the wire lugs replace if not in good condition than reconnect the wires. 15 With the equalizing valve in the manifold open, slowly open the high pressure and low-pressure isolations valves simultaneously. 16 Close the equalizing valve. 17 Observe fittings and arrest leakages if any, immediately. 18 Clean the workplace and site from where transmitter was removed and dispose the wastes as per the instruction for waste disposal. 19 Close the PTW | Pack | 1 |
| 177 | Temperature transmitter for motor couple | 1. Mechanical Inspection - Check transmitter housing for cracks or damage - Verify nameplate and measuring range - Inspect thermocouple terminals for tightness and oxidation 2. Electrical Inspection - Check 4–20 mA signal wiring - Verify 24 VDC power supply - Measure output current at zero condition (approximately 4 mA) 3. Zero Calibration - Disconnect the actual thermocouple - Connect the TC calibrator to the transmitter input - Simulate temperature at 0% of range (e.g. 0 °C) - Adjust ZERO until output reaches 4.00 mA - Verify the value on PLC/SCADA 4. Span Calibration - Simulate temperature at 100% of range (e.g. 400 °C) - Adjust SPAN until output reaches 20.00 mA - Check linearity at intermediate points: 25% – 50% – 75% 5. Loop & Signal Check - Verify scaling in PLC - Compare simulated value with displayed value - Check High / Low alarms 6. Completion - Disconnect the TC calibrator - Reconnect the actual thermocouple - Tighten all terminals - Close and seal the junction box | Pack | 1 |
| 178 | Encoder | 1. Check supply voltage and output signals - Measure the supply voltage to the encoder: 4.75 – 30VDC 2. Power off the system - Turn off the power supply to ensure safety during inspection and cleaning. 3. Check mechanical connections - Inspect the shaft coupling for any looseness, cracks, or wear. - Ensure the encoder is securely mounted and properly aligned with the shaft. 4. Clean the encoder surface - Use a dry cloth to wipe off dust and moisture on the encoder housing. - Check for signs of rust, cracks, or physical deformation. 5. Inspect cables and connectors - Check the connectors for oxidation, looseness, or broken pins. - Inspect cables for bends, cracks, or insulation damage. - Tighten all connection points as needed. 6. Restore power to the system - Reconnect all cables and connectors. - Restore power to the system. - Verify that the encoder is operating normally and that signal feedback is correct on the control display | Pack | 1 |
| 179 | Actuator | 1. To perform maintenance of the limit switch, dismantle the switch from object/target (With operational mechanism or without depends upon the type of sensor). 2. Before dismantling of limit switch make sure logic is override/forced (if required depends upon critically). 3. Isolate the electrical supply/power source & provide insulations to cables. 4. Note pre travel of limit switch 5. Note the initial position/alignment of limit switch. 6. Dismantle switch via unscrewing its support assembly/holder. 7. Check the operational mechanism of switch via operating it; lubricate it (if applicable). 8. Make sure operating force (torque) is enough to operate a mechanism, lubricate it (if applicable). 9. Make sure minimum return force (Torque) is enough to retract its mechanism, lubricate it if it applicable 10. Make sure the total travel of limit switch; lubricate it (if applicable). 11. Repeat accuracy of limit switch. 12. Reinstate the system 13. Fill record sheet. 14. Adjustment 15. To perform adjustment of limit switch, make sure total travel of switch (operational mechanism depend on type of switch). prior performing adjustment Remove interconnection of limit switches 16. Unscrew the loose holding support. 17. Adjust limit switch or its mechanism with referring measured/observed total travel of mechanism. 18. Repeat accuracy of switch to ensure operational ranges. | Pack | 1 |
| 180 | Solenoid valve | 1 Work Procedure 1.1 General 1.1.1 Inspect the instrument's pressure connection, cable gland, mounting, tubing’s, etc. 1.1.2 Close the isolation valve before the solenoid valve if the line is pressurized. 1.1.3 Clean the instrument with brush, CRC & waste cotton, or any similar cleaning item available 1.1.4 Remove the solenoid, disassemble it. 1.1.5 Clean the Plunger, Spool, spacer, O-ring (replace if required), spring (replace if required) Clean the instruments 1.1.6 Dry it & apply Silicon grease on movable parts and O-rings. 1.1.7 Assemble solenoid. 1.1.8 Mount back to its initial position 1.1.9 Make Power supply connections 1.1.10 Perform function test, Energies the coil and see if it is actuated and the valve is opening 1.1.11 Document the result of the activity. In co-ordination with operation personnel, cancel the PTWs to normalize instrument | Pack | 1 |
| 181 | Limit switch | 1. To perform maintenance of the limit switch, dismantle the switch from object/target (With operational mechanism or without depends upon the type of sensor). 2. Before dismantling of limit switch make sure logic is override/forced (if required depends upon critically). 3. Isolate the electrical supply/power source & provide insulations to cables. 4. Note pre travel of limit switch 5. Note the initial position/alignment of limit switch. 6. Dismantle switch via unscrewing its support assembly/holder. 7. Check the operational mechanism of switch via operating it; lubricate it (if applicable). 8. Make sure operating force (torque) is enough to operate a mechanism, lubricate it (if applicable). 9. Make sure minimum return force (Torque) is enough to retract its mechanism, lubricate it if it applicable 10. Make sure the total travel of limit switch; lubricate it (if applicable). 11. Repeat accuracy of limit switch. 12. Reinstate the system 13. Fill record sheet. 14. Adjustment 15. To perform adjustment of limit switch, make sure total travel of switch (operational mechanism depend on type of switch). prior performing adjustment Remove interconnection of limit switches 16. Unscrew the loose holding support. 17. Adjust limit switch or its mechanism with referring measured/observed total travel of mechanism. 18. Repeat accuracy of switch to ensure operational ranges. | Pack | 1 |
| 182 | Inclinometer | 1. External Inspection - Check sensor housing for cracks, deformation, or corrosion. - Verify mounting bracket and bolts are secure. - Ensure the sensor is firmly fixed and not loose. - Check cable, connector, and cable gland condition. 2. Electrical Inspection - Verify power supply voltage according to datasheet. - Check wiring terminals and connector tightness. - Inspect for damaged insulation or loose contacts. - Measure output signal wiring continuity. 3. Functional Test (Angle Measurement) - Power on the inclinometer. - Place the sensor at 0° reference position (horizontal or defined mechanical zero). - Verify output signal corresponds to 0° (e.g. 4 mA, 0 V, or zero value in PLC). - Slowly tilt the sensor to a known angle - Verify output signal changes smoothly without fluctuation. - Compare measured angle with reference tool (spirit level / angle gauge). 4. Signal Verification to PLC / SCADA - Check signal value in PLC (raw and scaled value). - Confirm scaling corresponds to actual angle range. - Verify alarm/trip thresholds - Ensure no signal loss or noise during movement. 5. Maintenance - Clean sensor housing and mounting area. - Clean connectors and reapply protection if needed. - Retighten mounting bolts and electrical terminals. 6. Reassembly & Completion - Restore all covers and cable glands. - Restore power supply. - Perform final functional check. 7. Acceptance Criteria - Stable and accurate angle output. - No abnormal signal fluctuation. - Secure mechanical installation and intact wiring. | Pack | 1 |
| 183 | Level transmitter | 1. External Inspection (Mechanical) - Check the sensor housing for cracks, damage, or corrosion. - Verify the installation position is according to the design (mounting height and orientation). - Check mounting brackets and bolts are securely tightened. - Inspect signal cables, cable glands, and junction box condition. 2. Electrical Inspection - Verify the power supply is correct (24 VDC). - Check the 4–20 mA signal wiring (+/–). - Measure the signal current: - No open circuit. - No abnormal fluctuation. - Check grounding / shielding. 3. Functional Test - Power on the sensor. - Change the actual water level (or simulate the level). - Verify that: - The output current changes linearly with the water level. - No signal delay or abnormal jumping occurs. - Compare the indicated level with the actual level. 4. Calibration 4.1 Zero Point (0%) - Set the water level to the lowest point (0% / Empty). - Check the output current: - Approximately 4 mA. 4.2 Span Point (100%) - Set the water level to the highest point (100% / Full). - Check the output current: - Approximately 20 mA. - Adjust the span if deviation is observed. 4.3 Intermediate Check - Check at 25% – 50% – 75% level points. - Ensure the error is within the allowable tolerance. 5. Signal Verification to PLC / SCADA - Check the raw 4–20 mA value. - Verify the level scaling (m, mm, %) in the PLC. - Check high and low level alarms (HH, H, L, LL). - Ensure stable indication. 6. Completion - Retighten all bolts and cable glands. - Seal the junction box properly. | Pack | 1 |
| 184 | Level switch | 1. External Inspection (Mechanical) - Inspect the float level switch housing for cracks, dents, or corrosion. - Inspect the float: - Ensure it moves freely without sticking. - Inspect the float rod / pivot shaft. - Check mounting brackets and bolts are securely tightened. - Inspect cable glands, signal cables, and the junction box. 2. Electrical Inspection - Verify the contact configuration (NO / NC / COM). - Inspect signal wiring, cable lugs, and terminal blocks. - Use a multimeter to check contact continuity: - Non-actuated condition. - Actuated condition. - Ensure there is no short circuit or open circuit. 3. Functional Test - Energize the control circuit - Actuate the float manually or change the actual liquid level. - Verify that: - Contacts open/close according to the design logic. - No contact delay or contact bouncing occurs. - Check the signal to the PLC / SCADA: - ON/OFF status is displayed correctly. 4. Calibration (Set Point Adjustment) - Float level switches are not calibrated as analog devices; calibration is performed by adjusting the actuation level. - Identify the required actuation level (H / L / HH / LL). - Adjust: - The installation position of the switch. - Change the liquid level to the actuation point and: - Record the ON level. - Record the OFF level. - Ensure that: - The actuation point meets the design requirement. - There is no false operation due to vibration or liquid turbulence. 5. Interlock & Alarm Check - Check high and low level alarm signals. - Verify interlock logic (if applicable). - Ensure the system responds correctly when the float is actuated. 6. Completion - Retighten all bolts and cable glands. - Properly seal the junction box. | Pack | 1 |
| 185 | PLC/WinCC/VFD program backup - PLC program backup | 1. Open the STEP 7 SIMATIC software, check the latest program, and perform a backup to a new file. | Pack | 1 |
| 186 | PLC/WinCC/VFD program backup - VFD program backup | 1. Open the starter software, connect to laptop, and perform a backup to a new file. | Pack | 1 |
| 187 | Communication | 1. External Inspection (Mechanical) - Inspect the cable route: - No breaks, crushing, or bending beyond the allowable bending radius. - Inspect the ODF and fiber distribution box: - Covers are properly closed, no moisture, no dust. - Inspect patch cords: - No breakage, no scratches on connector ends. - Check labels and fiber numbering according to the design. 2. Fiber Connector Cleaning - Disconnect the connector from the equipment. - Clean the ferrule using: - Isopropyl alcohol. - Dedicated cleaning tissue. - Allow to dry completely before reconnecting. 3. Continuity Test - Use a Light Source. - Check: - Ensure light passes through the fiber continuously. 4. Communication Signal Check - Reconnect the equipment. - Check: - Link LED indicators (TX/RX). - No LOS / LOF alarms. - Perform ping test / check SCADA data (if applicable). 5. Completion - Reconnect patch cords in the correct order. - Arrange cables neatly inside the ODF. - Close and seal the fiber distribution box. | Pack | 1 |
| 188 | CCTV | * General 1. System status check: Verify all cameras are online (100% operational) 2. Image quality check: Check clarity, noise, delay (Clear image, no lag) 3. Storage check: Verify HDD and recording (Continuous recording) 4. Camera cleaning: Clean lens and housing (No dust or blur) 5. Angle adjustment: Adjust viewing direction (Correct coverage) 6. IR check: Test night vision (IR working properly) * NVR/DVR 1. HDD inspection: Check SMART and bad sectors (No errors) 2. Data backup: Backup important data (Completed) *Network 1. Cable inspection: Check cable condition (Stable signal) 2. Ping test: Check latency (<5 ms) *Power 1. UPS check: Battery and backup time (As designed) | Pack | 1 |
| 189 | Pressure gause | A. Setup - Connect gauge to calibrator - Ensure no leakage - Set system at zero pressure B. Calibration Steps Step / Pressure Point / Action / Requirement 1. 0% / FS / Record / zero / = 0 2. 25% / FS / Apply pressure / Stable 3. 50% / FS / Apply pressure / Stable 4. 75% / FS / Apply pressure / Stable 5. 100% / FS / Apply pressure / Stable 6. 75% / FS / Decrease pressure / Check hysteresis 7. 50% / FS / Decrease pressure 8. 25% / FS / Decrease pressure 9. 0% / FS / Back to zero C. Error Calculation - Error (%FS) = Measured − Standard Full Scale × 100 - Error (%FS)= Full Scale Measured−Standard×100 D. Acceptance Criteria - Error ≤ ±1% FS (hoặc theo spec) - Kim di chuyển mượt, không giật - Sai số lên/xuống (hysteresis) trong giới hạn E. Adjustment (if required) - Condition / Action - Zero error / Adjust zero screw - Span error / Adjust span mechanism - Non-linear error / Replace gauge | Pack | 1 |
| 190 | Belt weigher | 1 Work Procedure 1.1 General 1.1.1 Check cable glands, blanking plugs for correct tightness. 1.1.2 Check the power supply, wire connections, connector & extension probe connectors and tighten them, contact cleaner or any other available carbon removal aid if connections found rusty & carbonized, if necessary, replaced them conditionally. 1.1.3 Clean the relative accessories like local field junction boxes with brush & waste cotton, or any similar cleaning aid item available. 1.1.4 Check supply voltages. 1.2 Conveyor Belt Calibration & Maintenance 1 Make sure the conveyor belt stops and hang warring signs before start of work. 2 Remove the side cover of conveyor belt to get access of load cell and limit switches. 3 First change the SELECTOR BUTTON from REMOTE to LOCAL, ask operator to run conveyor belt from Local. 4 Check for alarm on panel i.e.: belt misalignment, change broken and blockage. 5 If there is any Alarm STOP conveyor belt and resolve it, make sure there is no Alarm. When there is no alarm, START conveyor belt again. 6 Wait until the conveyor belt speed gets normal (0.26m/s). 7 For CALIBRATION of conveyor belt press the “MENU” button on the front panel, the first page of main menu will display. 8 Pressing “2” from Main Menu enters the Calibration Menu. 9 Move the cursor to ZERO CALIBRATION with Up/Down scroll keys and press ENT key to below menu. 10 Press “AUTO ZERO “soft key on the screen. 11 Press the “BGIN ZERO“ soft key on the screen to start the zero test. 12 When auto-zeroing is finished, press “SURE ZERO” button. 13 Repeat 10 and 11 steps 3 times and record the values. Error must be less than 0.2%. NOTE: During auto zeroing process, belt must be running, because complete zeroing process needs one revolution of belt running. If there is error in connection of sensor, or signal vibrates too large, then below menu will be displayed (please check for fault). 14 Stop the conveyor belt by press the OFF BUTTON, Install on panel 15 Before span calibration, standard weights must be loaded (12.8kg). In “Cal. data setup 1” under system main menu “3. System setup”, modify calibration method, select “weight cal” in simulated calibration, and enter “weights weight”. 16 For SPAN CALIBRATION Span Calibration menu is accessible by selecting “SPAN CALIBRATION” from the Calibration Menu, then press “ENT”. 17 Press the “AUTO SPAN” soft key under menu from the screen. 18 Press the “BGIN ZERO“ soft key on the screen to start the span calibration then Press “SURE SPAN” to save calibration .When completed. 19 Repeat step 16 and 18 three times. Record the values .The error must be Calibration 0.2%. | Pack | 1 |
| 191 | MV SWGR | A.Inspection and cleaning 1. Rack out the VCB 2. Clean the unit using a vacuum cleaner and wiping cloths. 3. Check all bolts using a torque wrench according to the manufacturer's standards. 4. Inspect and replace indicator lights if damaged. 5. Check wiring contacts and tighten terminal blocks. 6. Inspect and clean the busbars B.MV Switchgear Testing 1. Current transformer checks. 2. Voltage transformer checks. 3. Circuit breaker checks. 4. Testing of metering accuracy by secondary injection (Ammeter Check,Voltmeter Check,Energy Meter Check,Power Meter Check,,etc) 5. Perform functional testing for Relay 615 protection elements (50, 51, 51N, 27, etc.). | Pack | 1 |
| 192 | LV SWGR | 1. Rack out the MCC 2. Clean the unit using a vacuum cleaner and wiping cloths. 3. Check all bolts using a torque wrench according to the manufacturer's standards. 4. Inspect and replace indicator lights if damaged. 5.Check circuit breaker (CB) position and compare with local indicator lamp. 6.Check the contactor position and compare with local indicator lamp. 7.Check the current transformer (CT) for any looseness, signs of overheating, or partial discharge 8.Check the voltage transformer (VT) for any looseness or signs of overheating 9. Check wiring contacts and tighten terminal blocks. | Pack | 1 |
| 193 | Transformer | 1. Inspect, clean, and vacuum the transformer. 2. Inspect all wire connections for any signs of oxidation. 3. Inspect and clean the busbars. 4. Check all bolts using a torque wrench according to the manufacturer's standards. 5. Transformer internal resistance check 6. Measure insulation resistance (IR test). 7.Inspect and clean the temperature gauge | Pack | 1 |
| 194 | Motor 11kV | 1. Open the motor terminal box. 2. Clean the interior of the terminal box. 3. Check all bolts using a torque wrench according to the manufacturer's standards. 4. Measure the motor winding resistance. 5. Measure the insulation resistance (IR test). 6. Check the motor space heater power supply and the heating elements. 7. Inspect and clean the motor cooling fan | Pack | 1 |
| 195 | Motor 0.4kV | 1.Open the motor terminal box. 2. Inspect terminal contacts for any signs of oxidation. 3. Inspect and clean off all dust and debris. 4. Tighten all terminal blocks and wiring connections. 5. Measure the motor winding resistance. 6. Measure the motor insulation resistance (IR test). 7. Perform a load test; replace motor bearings if any shaft or bearing abnormalities are detected. 8. Inspect and clean the motor cooling fan | Pack | 1 |
| 196 | UPS,DC and PLC panel | 1. Open the panel and inspect the internal condition. 2. Inspect contacts and terminals for any signs of oxidation. 3. Clean and vacuum the interior thoroughly. 4. Tighten all control wiring connections 5. Replace cooling fans if damaged. | Pack | 1 |
| 197 | High Voltage Intermediate Junction Box | 1. Open the panel and inspect the internal condition. 2. Inspect contacts for any signs of oxidation. 3. Clean and vacuum the interior thoroughly. 4. Tighten all power terminal blocks and connections. | Pack | 1 |
| 198 | Inverter panel | 1. Open the panel and inspect the internal condition. 2. Inspect contacts and terminals for any signs of oxidation. 3. Clean and vacuum the interior thoroughly. 4. Tighten all control wiring connections 5. Replace indicator lights if damaged. 6. Replace cooling fans if damaged. | Pack | 1 |
| 199 | LCP | 1. Open the panel and inspect the internal condition. 2. Inspect contacts and terminals for any signs of oxidation. 3. Clean and vacuum the interior thoroughly. 4. Tighten all control wiring connections | Pack | 1 |

The above service price includes the supervisors, technicians/ equipment & tools, heavy equipment, consumables, … which are needed to complete the job.

The contractor is required to give the break-down unit price for each package with detail in following page.

- Man-power rate (which will be applied to pay for any arising job, out of scope in above package)

This will not be included in the total amount of maintenance package.

- To use as an add-off option for any arising work.

- Other costs like (transportation, machining) will be reimbursed based on actual if any.

| No | Category | unit | Unit Price (VND/excl. VAT) |
| --- | --- | --- | --- |
| 1 | Technician/ worker | Man/day |  |
| 2 | Supervisor | Man/day |  |
| 3 | Welder 3G/4G | Man/day |  |
| 4 | Welder 6G | Man/day |  |
| 5 | Scaffolder | Man/day |  |
| 6 |  |  |  |
| 7 |  |  |  |
| 8 |  |  |  |

- Technical Proposal includes

- Maintenance Procedure/ method statement/ ITP

- Safety measures

- Schedule of system

- Manpower mobilization

- Tools, machinery, heavy equipment, and consumable mobilization

- Reference documents

| No. | Document no. | Description |
| --- | --- | --- |
| 1 | VA2-CT00-P0EAA-610001 | O&M MANUAL_BOP_SHIP UNLOADER |
| 2 | VA2-CT00-P0EAD-650001 | O&M MANUAL_BOP_STACKER CUM RECLAIMER |
| 3 | VA2-CT00-P0ECC-620001 | O&M MANUAL_BOP_COAL HANDLING SYSTEM |

Annex 02_ PROPOSAL FORM

PHỤ LỤC 02_ BIỂU MẪU BẢN CHÀO GIÁ

(Company letterhead/Tiêu đề công ty)

Date/ Ngày tháng:

To: VUNG ANG II THERMAL POWER LLC (VAPCO)

Kính gửi: CÔNG TY TNHH NHIỆT ĐIỆN VŨNG ÁNG II (VAPCO)

Attn: Mr. Pham Ngoc Thach, Procurement & Contract Leader

Attn: Mr. Ha Jong Woo– GA & Contract Manager

We, _____(your company name)_______, undersigned, hereby offer to supply Unit 1 overhaul services- Coal Handling System to Vung Ang II Thermal Power LLC in compliance with VAPCO’s RFP #VAPCO/PS-50182-4 dated 15 April 2026.

Chúng tôi, ____(tên đơn vị)________, ký tên dưới đây, chào giá cung cấp các dịch vụ tiểu tu Tổ máy 1-  Dây chuyền than cho Công ty TNHH Nhiệt điện Vũng Áng II tuân thủ Yêu cầu chào giá của VAPCO số VAPCO/PS-50182-4 ngày 15/04/2026.

| No. Số | Item* Hạng mục | Unit and Quantity Đơn vị và Số lượng | Completion time Thời gian hoàn thành | Unit price Đơn giá (VND) | Total price Thành tiền (VND) |
| --- | --- | --- | --- | --- | --- |
| I |  |  |  |  |  |
| 1 |  |  |  |  |  |
| 2 |  |  |  |  |  |
| 3 |  |  |  |  |  |
| … |  |  |  |  |  |
| Total Price (excluding VAT)/ Tổng Giá trị (chưa bao gồm VAT) |  |  |  |  |  |

* Bidders to quote the corresponding items covered under each item of the Scope of Service

- Terms and conditions/ Các điều khoản và điều kiện:

The price is exclusive VAT but inclusive of all applicable taxes, duties or other applicable expenses

Giá chưa bao gồm thuế GTGT nhưng đã bao gồm các loại thuế, phí và các chi phí liên quan khác.

Total payment will be made within 30 days of receiving the valid payment documents as outlined in the Contract Form.

Thanh toán trọn gói sẽ được thực hiện trong vòng 30 ngày làm việc kể từ ngày nhận được chứng từ thanh toán hợp lệ theo quy định của Hợp đồng.

- Contact Person/ Đầu mối liên hệ:

Contact person	:			Position

Đầu mối liên hệ: 			Chức danh

Telephone	: 			Email:

Số điện thoại: 				Email:

|  | Legal representative of Bidder Người đại diện pháp lý của Nhà thầu [Full name, position, signature and seal [Họ tên, chức vụ, chữ ký và con dấu] |
| --- | --- |

Annex 03_ CONTRACT FORM

PHỤ LỤC 03_ MẪU HỢP ĐỒNG

(from the next page/ từ trang sau)