### 2. TECHNICAL REQUIREMENTS

### 2.1. General introduction to the Project and the Tender package

### 2.1.1. Objectives of the construction project

The "Quynh Luu 500kV Substation and Connecting Transmission Line" project was invested in and constructed with the following objectives:

- Ensuring a safe and reliable power supply for the power load in Nghe An province, providing a large amount of power shortfall of approximately 4000-5000 MW to the power load after the 220kV Quynh Luu and 220kV Quy Hop substations.

- To reduce construction investment costs for the grid-connection works of the Quynh Lap Thermal Power Plant in the event that this project proceeds to construction investment.

- This will help to improve transmission capacity on the Central-Northern cross-section, thereby contributing to ensuring electricity supply in the North and relieving the burden of renewable energy for the Central and Southern regions.

- Strengthening system connectivity and improving the safety, reliability, and quality of electricity for the regional power grid.

- Minimize power losses in the transmission grid and increase overall business efficiency.

- Creating strong connections between regions within the power system enhances the safe and stable operation of the national power grid.

- Enhancing the stability of electricity supply, reducing power losses and energy losses in the system, and improving the production and business efficiency of Vietnam Electricity Group.

### 2.1.2. Project scope and construction location

a. Location of the power line construction project:

The "Quynh Luu 500kV Substation and Connecting Transmission Line" project is being implemented in Nghe An province, specifically in the following locations:

  - Quynh Tam Commune;

  - Quynh Son Commune;

  - Quynh Van Commune.

b. Scale of the connection transmission line section:

The 500kV transmission line connects to the Quynh Luu 500kV substation:

The 500kV transmission line connecting to the Quynh Luu 500kV substation is being constructed in the communes of Quynh Tam and Quynh Son, Nghe An province, and includes two parallel 500kV transmission lines connecting to the Quang Trach - Quynh Luu - Thanh Hoa 500kV transmission line.

- Branch 1: The 500kV connecting line starts from the Quynh Luu 500kV substation and ends at tower No. 464 of the Quang Trach - Quynh Luu 500kV line;

- Branch 2: The 500kV connecting line starts at the Quynh Luu 500kV substation and ends at tower No. 01 of the Quynh Luu - Thanh Hoa 500kV line.

The two connecting 500kV transmission lines have the following specific dimensions:

Branch 1:

| Starting point | - : Pooctich TBA 500kV Quynh Luu; |
| --- | --- |
| End point | - : Tower No. 464 (D1) on the 500kV Quang Trach – Quynh Luu power line; |
| Voltage level | - : 500kV; |
| Circuit number | - : 02 circuits; |
| Length | - : approximately 0.657 km; |
| Conductors | - : Use 4xACSR 500/64 conductors of the same conductor type on the 500kV Quang Trach - Quynh Luu transmission line. Other parameters and technical requirements of the conductors are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Overhead ground wires | - : Use PHLOX-116 lightning protection wire and OPGW120 combined lightning protection wire with 36 optical fibers of the same wire type, on the 500kV Quang Trach - Quynh Luu transmission line. The parameters and technical characteristics are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Insulators | - : Use suspension insulators manufactured according to IEC standards; |
| Towers | - : Equal-leg angles shape steels and hot-dip galvanized, connected by bolts; |
| Foundations | - : Cast-in-place reinforced concrete. |

Branch 2:

| Starting point | - : Pooctich TBA 500kV Quynh Luu; |
| --- | --- |
| End point | - : Pole 01 (D2) on the 500kV Quynh Luu – Thanh Hoa power line; |
| Voltage level | - : 500kV; |
| Circuit number | - : 02 circuits; |
| Length | - : Approximately 0.797 km; |
| Conductors | - : Use 4xACSR 400/51 conductors of the same conductor type on the 500kV Quynh Luu – Thanh Hoa transmission line. Other parameters and technical requirements of the conductors are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Overhead ground wire | - : Use PHLOX-116 lightning protection wire and OPGW 120 combined lightning protection wire with 36 optical fibers, matching the wire type on the 500kV Quynh Luu – Thanh Hoa transmission line. Other technical specifications and requirements for lightning protection wire are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Insulators | - : Use suspension insulators manufactured according to IEC standards; |
| Towers | - : Equal-leg angles shape steels and hot-dip galvanized, connected by bolts; |
| Foundations | - : Cast-in-place reinforced concrete. |

The 220kV transmission line connects to the Quynh Luu 500kV substation:

The 220kV transmission line connecting to the 500kV Quynh Luu substation was constructed in the communes of Quynh Tam, Quynh Son, and Quynh Van in Nghe An province. Its starting point is the 220kV Pooctich at the 500kV Quynh Luu substation, and its end point is the 220kV Quynh Luu substation.

| Starting point | - : Pooctich TBA 500kV Quynh Luu; |
| --- | --- |
| End point | - : Connecting the Nghi Son - Quynh Luu 220kV transmission line; |
| Voltage level | - : 220kV; |
| Circuit number | - : 4 circuits; |
| Length | - : Approximately 9.97 km; |
| Conductors | - : Use 2xACSR 330/43 conductors. Other specifications and technical requirements for conductors are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Overhead ground wire | - : Use 02 lightning protection wires combined with OPGW 90 fiber optic cable. Other technical specifications and requirements for lightning protection wires are as stipulated by EVNNPT in Decision No. 1684/QD-EVNNPT dated August 25, 2025; |
| Insulators | - : Use suspension insulators manufactured according to IEC standards; |
| Towers | - : Equal-leg angles shape steels and tube steel shape, hot-dip galvanized, connected by bolts; |
| Foundations | - : Cast-in-place reinforced concrete. |

Relocation and restoration of the 110kV lines 171E15.30 T220kV Quynh Luu - 171E15.2 Nghia Dan and the 110kV line 172E15.30 T220kV Quynh Luu - 172E15.3 Quy Hop:

| Starting point | - : New 2-circuit tower between 2 110kV transmission lines: Route 171E15.30 T220kV Quynh Luu - 171 E15.2 Nghia Dan (near VT41) and Route 172 E15.30 T220kV Quynh Luu – 172 E15.3 Quy Hop (near VT46); |
| --- | --- |
| End point | - : New 2-circuit tower between 2 110kV transmission lines: Route 171E15.30 T220kV Quynh Luu - 171 E15.2 Nghia Dan (near VT44) and Route 172 E15.30 T220kV Quynh Luu - 172 E15.3 Quy Hop (near VT49); |
| Voltage level | - : 110kV; |
| Circuit number | - : 02 circuits; |
| Length | - : Approximately 0.67 km; |
| Conductors | - : Use ACSR 300/39 cable; |
| Insulators | - : Use vertical insulators manufactured according to IEC standards; |
| Towers | - : Equal-leg angles shape steel, hot-dip galvanized, connected by bolts; |
| Foundations: | - : Cast-in-place reinforced concrete. |

### 2.2. Technical requirements

The following technical requirements are to be read in conjunction with the tower design drawings and the Project Technical Specifications (CDKT). If there are any discrepancies with the corresponding contents in the Design drawings and CDKT, the contents in the Design drawings shall prevail.

### 2.2.1. Main works included in the bidding package

- Preparation for processing (manufacturing);

- Machining (manufacturing);

- Assembly of sample towers: The contractor may propose a method for inspecting sample towers according to the contractor's fabrication procedure, ensuring the quality of the towers meets the design requirements and contract specifications, and preventing errors that could affect the project schedule (the contractor is responsible for assembling the sample towers themselves).

- Correct any errors or defects (if any);

- Mass production and manufacturing;

- Inspect fabricated products;

- Inspect the product after hot dip galvanizing;

- Packaging and shipping.

Towers will be manufactured and inspected in accordance with the " Regulations on the design and manufacture of towers and bolted structures used for Transmission lines and substations in Vietnam Electricity Group (EVN)" issued with Decision No. 428/QD-EVN dated March 26, 2025, of Vietnam Electricity Group.

### 2.2.2. Standards

All details, materials, manufacturing processes, and testing specifications in this tender document must comply with the project documentation (Technical Requirements, Technical Specifications, Standards, Manuals, and Technical Data, etc.). Documents listed below or equivalent applicable standards approved by the Buyer shall, in case of any standard conflict, be governed by the standards in the design documents.

Standards for steel structure work:

- TCVN 5575: 2024: Standard for the design of steel structures;

- TCXDVN 170-2007: Steel structures - Fabrication, assembly and acceptance testing - Technical requirements;

- TCVN 12002:2020: Steel structures - Fabrication and quality control;

- TCVN 13194:2020: Steel structures - Erection and acceptance testing;

- TCVN 8298:2009: Hydraulic structures - Technical requirements in the manufacture and assembly of mechanical equipment and steel structures;

- TCVN 2248-1977: Metric threads - Basic dimensions;

- TCVN 1917-1993: Metric threads - Clearance fits - Tolerances;

- TCVN 1916-95: Bolts, screws, studs and nuts - Technical requirements;

- TCVN 1889-76: Hexagon head bolts (semi-finished) - Dimensions;

- TCVN 1897-76: Hexagon head nuts (semi-finished) - Dimensions;

- TCVN 2061-77: Washers - Dimensions;

- TCVN 134-77: Washers - Technical requirements;

- TCVN 130-77: Spring washers - Dimensions and technical requirements;

- TCVN 128-63: Fastening components - Rules for acceptance, packaging and labeling;

- TCVN 1691:1975: Manual electric arc welding;

- TCVN 3223-2000: Welding electrodes for low-carbon steel and low-alloy steel - Symbols, dimensions and general technical requirements;

- TCVN 197-1:2014: Metallic materials - Tensile testing - Part 1: Room temperature test method ;

- TCVN 198:2008: Metallic materials - Bending test;

- TCVN 1765-1975: Ordinary structural carbon steel - Steel grades and technical requirements;

- TCVN 7571-1:2019: Hot-rolled structural steel - Part 1: Equal-leg angles steel;

- JIS G3101: Japanese Industrial Standard, Rolled steel for general structure;

- JIS G3444: Carbon steel tubes for general structural purposes

- JIS G4051 Carbon steels for machine structural use

- GB-15191-2018 Low-alloy high-strength structural steel

- GBT-700-2006 Carbon structural steels

- JIS G3192: Japanese Industrial Standard, Dimensions, mass and permissible variations of hot rolled steel sections;

- Standards to produce power transmission steel tube towers, April 2015, by the Japan Steel Tower Association.

- Standard TCVN 11244-8:2015 ISO 15614-8:20002 Technical specifications and acceptance of welding procedures for metallic materials - Welding procedure testing - Part 5: Tube welding in plate-tube joints.

- Government Decree 14/2014/ND-CP detailing the implementation of the Electricity Law regarding electrical safety;

- Decree No. 51/2020/ND-CP on amending and supplementing a few articles of Decree 14/2014/ND-CP;

- Regulations on the design and manufacture of steel towers and bolted steel structures used for transmission lines and substations within the Vietnam Electricity Group (EVN), issued together with Decision No. 428/QD-EVN dated March 26, 2025, by the Vietnam Electricity Group;

- 18 TCN 04-92: 500kV transmission lines - Hot-dip galvanizing of towers.

- The towers are hot-dip galvanized, complying with the regulations issued under Decision No. 428/QD-EVN, which stipulates the design and manufacture of steel towers and bolted steel structures used for transmission lines and substations within the Vietnam Electricity Group (EVN).

- 11 TCN-19-2006: Electrical Equipment Regulations - Part II: Power Line Systems;

- And other equivalent standards (if any).

(In cases where different standards provide the same guidance on a particular issue, the worst-case scenario calculation must be performed, while the safest conditions must be applied.)

- If the contractor is accepted to manufacture towers according to standards, using equivalent materials (standards and materials as offered by the contractor in the Bid Submission):

  - i) If the quantity of towers increases compared to the quantity of towers manufactured according to the basic standard specified in the tender drawings in Bid Documents, the contractor shall be fully responsible without incurring any additional costs;

  - ii) If the quantity of towers is reduced compared to the quantity of towers produced according to the basic standard specified in the tender drawings in Bid Documents, but still meets the technical requirements equivalent to the basic standard in the tender drawings in Bid Documents, the contractor shall be liable for a corresponding reduction in quantity and value.

  - iii) For changes in geometric dimensions, symbols, structural conditions, connections, etc., compared to the Construction Drawings in accordance with equivalent standards and materials proposed by the contractor in the Bid Submission, the contractor must prepare an appendix and detailed implementation drawings, proposing corrective measures and solutions for the Design Consultant and the Employer to review and approve.

### 2.2.3. Physical characteristics of steel

- Density : 				7850 (kG/m3)

- Coefficient of thermal expansion : 	0,12x10-4 (C-1)

- Elastic modulus E: 				2,1x106 (kG/cm2)

- Shear modulus G: 				0,81x106 (kG/cm2)

- Lateral expansion coefficient: 		0,3

### 2.2.4. Mechanical properties of steel

- The materials used to manufacture utility poles are specified in the towers manufacturing design drawings. The strength of the steel used to manufacture the towers is as follows:

- Equal-leg angle with flange width < 100mm uses common steel with the following yield strength and tensile strength:

- Steel grade SS400 according to JIS G3101; CT38 according to TCVN 1765-75 or equivalent in terms of mechanical properties, chemical composition, and elongation.

- Standard strength according to yield limit fy: 245 N/ mm² with  16 mm; 235 N/mm² with 16 mm < 40 mm

- Standard strength according to tensile strength limit fu: 400 N/mm2.

- Equal-leg angle with flange width of 100mm uses high-grade steel with the following yield strength and tensile strength:

- SS540 steel grade according to JIS G3101 standard or equivalent in terms of mechanical properties, chemical composition, and elongation.

- Standard strength according to yield limit fy: 400 N/mm2 (δ 16mm)

- Standard strength according to yield limit fy: 390 N/mm2 (16 < δ 40mm)

- Standard strength according to tensile strength limit fu: 540 N/ mm²

- Standard strength steel plates:

- Steel grade SS400 according to JIS G3101 or equivalent in terms of mechanical properties, chemical composition, and elongation.

- Standard strength according to yield limit fy 	: 245 N/mm2 (δ ≤ 16mm)

- Standard strength according to yield limit fy 	: 235 N/mm2 (16 < δ ≤ 40mm)

- Standard strength according to yield limit fy 	: 215 N/mm2 (40 <δ≤ 100mm)

- Standard strength according to yield limit fy 	: 205 N/mm2 (δ > 100mm)

Standard strength according to tensile strength limit fu	: 400 N/ mm²

- Steel tubes with a diameter < 139.8 mm should be of grade STK400 according to JIS G3444:2021 or equivalent, with mechanical properties, chemical composition, elongation, standard yield strength ≥ 235 N/mm², and tensile strength ≥ 400 N/mm².

- Steel tubes with a diameter > 139.8 mm should use grade STK540 according to JIS G3444:2015 or equivalent mechanical properties, chemical composition, elongation, with a standard yield strength ≥ 390 N/mm² and tensile strength ≥ 540 N/mm².

- High-grade steel plates using grade SM490YA according to JIS G3106:2024 or equivalent mechanical properties, chemical composition, elongation:

- For thicknesses δ ≤ 16mm, the standard yield strength is ≥ 365N/mm², and the tensile strength is ≥ 490N/mm².

- Thickness 16 < δ ≤ 40 has a standard yield strength ≥355N/mm², tensile strength ≥ 490N/mm².

- Thickness 40 < δ ≤ 75 has a standard yield strength ≥ 335N/mm², tensile strength ≥ 490N/mm².

- The specific type of steel to be used will depend on the thickness and other factors, as specified in the design drawings provided.

### 2.2.5 . Connection

a. Welded connection

- Manual electric welding according to TCVN1691-1975, T6 and T9 weld type, using E43 1 welding rod (for steel grade CCT38 or SS400 or equivalent) and E51 1 welding rod (for steel grade SS540 or equivalent) according to TCVN3223-2000 or a type with equivalent technical characteristics.

- Complex details such as the base plate must be assembled and tack-welded before final welding. Both tack-welding and final welding use electric arc welding, employing intermittent welding technology to avoid thermal deformation.

- Welding and weld inspection shall be carried out in accordance with TCVN 12002:2020; TCVN 13194:2020; and TCXDVN 170:2007.

b. Bolts, nuts, and washers

* Bolts

- Bolt strength grade 8.8 or higher for structural connection bolts.

- The bolts supplied must be 100% new and meet the following standards and specifications:

- Grade 8.8 connection bolts:

- The calculated shear strength fvb 	: 332 N/ mm².

- Calculated tensile strength ftb		: 448 N/mm2.

- Bolts are manufactured according to TCVN 1889-76 standards for bolts Ø <20mm and TCVN 1876-76 standards for bolts Ø 20mm.

- Thread conforms to standard: TCVN 2248-77.

- Tolerance according to standard: TCVN 1917-1993.

- Technical requirements according to standard: TCVN 1916-1995.

- Bolt sets shall include: 1 bolt, 1 nut, 1 flat washer, and 1 spring washer.

* Nuts

- The nuts are designed for strength grade 8 with bolts strength grade 8.8.

- Nuts are manufactured according to TCVN 1897-76 standards for bolts Ø <20mm and TCVN 1896-76 standards for bolts Ø 20mm.

- Thread conforms to standard: TCVN 2248-77.

- Tolerance according to standard: TCVN 1917-93.

- Technical requirements according to standard: TCVN 1916-1995.

* Washers

- Flat washers are made of CT3 steel or a type with equivalent technical characteristics, complying with TCVN 2061-1977 (machining standard) and TCVN 134-1977 (technical requirements).

- Spring washers are made of 65 steel or a type with equivalent technical specifications and are machined in accordance with TCVN 130-1977.

- Acceptance testing, packaging, and labeling comply with TCVN 128-1963 standards.

- The bolt threads must protrude beyond the tightened part of the nut, with this protrusion being at least one nut's length. Bolts, nuts, and washers must all be zinc-plated with a thickness that complies with the regulations issued under Decision No. 428/QD-EVN.

* Step bolts

- Strength level: 5.6 (T step bolts)

- Calculated shear strength fvb: 210 N/ mm²

- Calculated tensile strength ftb: 225 N/ mm²

- Tensile strength limit σb: 500 N/mm2

- Yield strength σch: 300 N/mm2.

- The ladder is attached to the two main members of the tower with step bolts from base to top, as shown in the detailed drawings provided in the "Construction Drawings" phase.

- The ladder leg bolts consist of: 1 bolt, 2 nuts, and 2 flat washers.

- All types of bolts, nuts, washers, and their combinations must be specified by the Designer and comply with the specifications in the final approved manufacturing drawings.

### 2.2.6. General material requirements

- Steel used for the fabrication of power poles shall be free from lamination corrosion and pitting. Only light surface oxidation in the form of discoloration or powdery oxide dust adhering to the surface is permitted.

- The steel used must be of good quality; its physical properties must not change or corrode during hot-dip galvanizing.

- All steel bars used for processing and fabricating towers and steel structures for electrical works (transmission lines, substations, power plants) shall be fabricated from continuous members without splices. The contractor must take samples in accordance with current regulations to test the mechanical properties of the steel; the cost for this is included in the bid price. Basically, as follows:

- Mechanical testing on steel samples.

- The required tests shall include flexural strength, ultimate tensile strength, and percentage elongation.

- Mechanical and galvanizing tests will be performed on the bolt and nut samples.

- The Contractor shall provide the Buyer with certificates of steel manufacturing quality and the basic characteristics of the steel types.

- The buyer will take random samples of the manufactured material for testing. The testing will be conducted by a specialized agency, and if the material fails to meet the testing requirements, the entire batch must be discarded.

### 2.2.7 . Technical requirements for the fabrication of steel columns

a. Preparation for processing

- According to the drawings (to be provided during the Construction Drawing phase after award of the contract), the Contractor shall check and review the dimensions of the structural details of the tower, the dimensions of the tower leg, and the base plate connecting to the foundation. The Contractor shall verify the accuracy of the wiring details attached to the tower according to the awarded insulator string diagram. The sample tower shall be fabricated in strict accordance with the issued drawings. The sample tower shall be fully assembled and internally accepted by the Contractor to prevent errors during mass production. The Contractor shall provide the Employer with a copy of the internal sample tower acceptance report during the payment acceptance process.

- In case of discrepancies or problems arising related to the tower, the Contractor must report to the Employer and the Consultant before commencing mass production for resolution. Failure to report to the Investor will be understood as not having any issues, and the Contractor will bear all costs related to the production and erection of the faulty tower.

- The contractor needs to check and verify the suitability of the stub bars and anchor bolts for each column foundation location.

- All discrepancies found in the drawings (differences in geometric dimensions, symbols, structural conditions, etc.) must be documented by the Contractor in an appendix and a proposal for correction and remediation must be submitted to the Design Consultant and the Employer for review and approval. The Contractor shall bear the cost of materials and labor for correction, rework, and reassembly.

b. Fabrication

b1. General requirements

- The surface of the steel must be flat, free from pitting, rust, warping, blistering, hot rolling, or other defects. Steel shall be of sufficient length to fabricate the members, and welding splices shall not be permitted. Joining bars with bolts will only be done individually and at specific locations as per the design drawings. Drilling, cutting, punching, pressing and bending of components shall be carried out accurately to facilitate easy erection of the columns on site.

- The fabrication complies with the Regulations on the Design and manufacture of steel towers and bolted steel structures used for transmission lines and substations in Vietnam Electricity Group (EVN), issued together with Decision No. 428/QD-EVN dated March 26, 2025, of Vietnam Electricity Group.

- Fabrication, assembly and acceptance shall comply with TCVN 12002:2020, TCVN 13194:2020 and TCXDVN 170:2007.

b2. Cutting

- The cut edges of steel tower components must be smooth, without roughness or burrs. Cutting steel profiles or plates to create sharp angles less than 60 degrees is prohibited to avoid accidents during transportation and installation.

- Steel members must be cut mechanically; other thermal cutting methods are not permitted. For steel with a thickness of 14 mm or greater used for plates, base plates, and plates with curved corners that cannot be cut by machine, gas cutting may be used, followed by reworking by machining. Members and plates with a thickness less than 14mm shall be cut using CNC machines.

b3. Bending

- When bending parts, the bending and shaping operations are performed at temperatures between 850C and 950°C, followed by natural cooling with air to prevent warping or cracking. Under no circumstances shall arc welding build-up be used for heating during steel straightening and bending.

- The Contractor shall use a reliable thermometer or other measuring instrument to check the temperature above. Any proposed measuring instrument must be submitted to the Consultant for approval and may only be used once approved.

- When bending equal-angle steel, the material in the bent area (the angle of the L-shaped steel) must be deformed by grinding to remove sharp edges. The minimum grinding length is 1mm, and the minimum distance from the bending axis is 40mm (along the bar) and 12mm (along the bar's width) from the bending point.

- Equal angle steel members with a thickness δ ≤ 8 mm requiring cold bending shall be pre-formed using a template with a radius equal to that of the member to be bent. The template plate shall have a thickness not less than three (3) times the thickness of the plate to be bent. Cold bending shall only be permitted when the bending angle does not exceed 10°. After bending, magnetic particle testing for cracks shall be carried out on at least 2% of the products of each batch. A batch is defined as the quantity of components cold bent within one day. Magnetic particle inspection for cracks shall be conducted along the normal edges of the curved portion over a distance of at least 15 mm on each side of the bend. Any component shall be rejected if non-linear particle indications or signs of cracking are observed during inspection using a magnifying lens with a minimum magnification of 5×. In the event of defects, all remaining components of the same batch shall be inspected in the same manner at no additional cost. The cost of the magnetic particle tests described above shall be included in the fabrication and erection costs, and the Engineer/Consultant reserves the right to inspect bent components in excess of the quantity specified above at no additional cost.

b4. Creating bolt holes

- Holes shall be drilled using guides and jigs or a CNC machine line to increase accuracy. The drill bits and jigs used for this work must be kept sharp enough to create round holes without sharp edges, wrinkles, etc. All bolt holes must meet the allowable tolerances.

- The bolt holes must be round, and the diameter of a single hole before plating must not exceed 1.6 mm of the bolt diameter for all bolt sizes (except those clearly indicated on the drawing). The bolt holes must be vertically cylindrical, perpendicular to the steel plane (bolt holes must not be oblique).

- The hole-making process does not deform, warp, or damage the steel structure surrounding the hole.

b5. Welding

- Only the plate may be welded together, or the plate to steel profiles, such as base plates or components connecting to accessories, or as specified in the manufacturing design drawings.

- Welding splices of tower members or overlapping welding of plates onto each other or onto other components are prohibited. Grooving of steel bars for bending and subsequent welding is also prohibited. All individual components must be formed from a single steel bar (or plate) without any welds.

- The welding procedure must be followed correctly according to regulations. The materials (welding rods) must be specified in advance.

- Welds must be uniform in height and smooth, free from rust, debris, grease, paint, or deep corrosion. The welds must not be porous or poorly filled. After melting the welding material, all spatters must be removed, or it can be gently tapped with a hammer and brushed away with a wire brush.

- All welds must be inspected ultrasonically after completion and certified. The welded plates or bars must be flat and straight, free from warping or deformation.

b6. Join the segments using angle steel.

- The joining of steel bars must comply with the instructions given in the 
steel tower fabrication drawings.

- If the joining bar is placed inside the connecting bar, the joining bar must be beveled to a thickness equal to the inner radius of the connecting bar.

- If the joining bar is placed outside the connecting bar, the end of the connecting bar must be beveled and dried, with the bevel thickness equal to the inner radius of the joining bar.

- Each end of the connecting bar must have a minimum of 4 bolts.

b7. Identification Marking

- Before galvanizing, each component of the tower must be stamped with an embossed mark indicating that it is a specific component within a particular tower, corresponding to its number in the approved drawing. Additionally, each component must be stamped with the manufacturer's name for management purposes during construction, operation and maintenance.

- The marking system used to identify tower members must ensure that no marking is duplicated within a tower type.

- The markings must be easily legible after galvanizing and do not adversely affect the strength of the component. The markings should be placed in a location where they will not be obscured by other parts during erection.

- Bolt marking is done at the head of each bolt to identify the manufacturer, type, size, length, and thread length. The markings can be engraved or embossed.

- To facilitate assembly, the stamping location is standardized on the outer surface of the part (at the working position):

- Marking shall be applied at the upper end for vertical and diagonal members.

- Marking shall be applied at the left end for horizontal members.

- Marking shall be applied at the upper corner of the plates

- The stamp must comply with Regulation 169NL-BQL:

- The minimum height of the letters and numbers on the stamp is 12mm.

- The minimum mark depth must be 1mm.

b8. Galvanizing

- The galvanizing line and technology of the steel pole manufacturer shall meet at least the following requirements:

- The galvanizing tank must have internal dimensions of 12m x 1m x 0.85m.

- A clean water supply system sufficient to meet galvanizing requirements shall be provided.

- Automatic temperature control should be provided.

- A fluxing system should be provided.

- The corrosion protection method for the steel structure of the tower shall be hot-dip galvanizing carried out after completion of all fabrication processes, including member and component numbering, cutting, drilling, grinding, bending, welding, or any other manufacturing operation. Prior to galvanizing, all steel members intended for tower fabrication shall be thoroughly cleaned of rust, oil, dust, and any adherent contaminants from their surfaces. All steel components shall be galvanized individually, member by member and part by part. Any members warped or distorted after galvanizing shall be straightened or rejected prior to delivery. The preparation and hot-dip galvanizing process shall not cause distortion or any effects that may adversely influence the mechanical and physical properties of the material.

- Hot-dip galvanizing shall comply with Standard 18TCN-04-92 and the regulations issued under EVN Decision No. 428/QĐ-EVN, or other equivalent standards. The zinc coating thickness shall conform to the requirements specified in the project documents (drawings, technical specifications, etc.). Where no specific requirement is given, the average coating thickness shall be as specified in the following table:

| Type of detail | Average plating thickness ( m) |
| --- | --- |
| Details of the steel column: thickness ≥ 6mm | 110 |
| Details of steel columns: thickness < 6mm | 100 |
| Bolts, nuts, washers | 55 |

- The minimum local coating thickness shall not be less than 90% of the specified average coating thickness. The maximum coating thickness (excluding bolts and nuts) shall not exceed 200 µm.

- The zinc used for galvanizing shall have a minimum purity of 98.5%. The coating surface shall be uniform and smooth, free from blowholes, slag inclusions, lumps, or other defects. Any members warped or distorted after galvanizing shall be straightened or rejected prior to delivery.

- The uniformity of the zinc coating shall be verified by instrumental measurement. The coating shall be firmly adherent, smooth, and even, with no blistering, lumps, roughness, bare spots, black stains, acid marks, slag, or any other defects.

- The quantity of materials in each galvanizing batch and the test specimens for each batch shall be clear and readily identifiable by appropriate marking. The test specimens shall consist of two (2) or more separate pieces, each having a minimum coated surface area of 2,600 mm², cut from the material used for fabrication of the tower components.

- If any of the test specimens taken from a batch fail to meet the minimum coating mass/thickness required by the galvanizing standard, then all members in that galvanizing batch shall not meet requirement.

- After galvanizing, all materials for steel tower fabrication shall be treated with a Sodium Dichromate solution or Preton W20 solution to prevent the formation of white rust. If clear evidence of white rust is observed on any steel components, the Employer shall require the Contractor to carry out the necessary inspections and tests to determine the extent of damage, if any, and to implement corrective measures.

- Any materials on which the zinc coating has been damaged shall be re-galvanized, unless the damage is local and can be repaired using an approved zinc coating repair compound. In such cases, the repair compound shall be applied strictly in accordance with the manufacturer’s instructions.

- Welding slag or acid/flux spills shall be removed immediately, and the work shall be carried out in such a manner as not to damage the adjacent coating or the base metal. Any parts for which the zinc coating becomes damaged after being re-dipped twice shall be rejected.

- Any galvanized component found to be defective or imperfect shall be replaced. The Contractor shall bear all costs associated with the replacement of defective components.

- The Contractor shall provide equipment for measuring zinc coating thickness or shall agree with the Employer on an approved galvanizing test method.

- The Contractor shall perform galvanizing tests on steel samples, with all costs included in the bid price. The required tests shall include determination of coating mass, adhesion, and uniformity characteristics of the zinc coating.

- Mechanical and galvanizing tests shall also be carried out on bolt and nut samples.

- The galvanized coating shall ensure a minimum service life of forty (40) years.

b9. Bolt tightening torque:

- Bolts of the tower shall be tightened sufficiently to ensure good contact between the faying surfaces. The tightening torque shall comply with Clause 4.4.5 of Standard TCXDVN 170-2007 (Steel structures – Fabrication, erection and acceptance – Technical requirements), specifically as follows: During bolted assembly, the bolts shall be tightened, and the remaining holes shall be aligned using erection pins. The tightness of the bolted joint shall be checked by means of a 0.3 mm thick feeler gauge, which shall not be able to be inserted more than 20 mm into the gap.

- In addition to the above inspection method, a calibrated torque wrench may be used to verify that the bolts have been tightened to the required tightening force/torque for each type of bolt in accordance with the table below (note that after tightening, the separated edges of the spring washer shall remain in the same horizontal plane).

Bolt tightening torque table according to TCVN 8298:2009

| No. | Type of bolt | Tightening torque (Nm) |  |
| --- | --- | --- | --- |
|  |  | Durability level 5.6 | Durability level 8.8 |
| 1 | M12 | 38.0 | 81.1 |
| 2 | M16 | 91.8 | 195.9 |
| 3 | M20 | 179.0​ | 382.0 |
| 4 | M22 | 239.0 | 510.0 |
| 5 | M24 | 307.4 | 656.0 |
| 6 | M27 | 449.0 | 958.0 |
| 7 | M30 | 562.5 | 1200.0 |

b10. Tolerances

- Permissible deviations in shape are based on: Regulations on the design and manufacture of steel poles and bolted steel structures used for transmission lines and substations in Vietnam Electricity Group (EVN) issued with Decision No. 428/QD-EVN dated March 26, 2025, of Vietnam Electricity Group, and the Standard for the production of steel transmission tower tubes, April 2015, of the Japan Steel Tower Association.

- Allowable shape deviations:

- For flat plate components, curvature is measured as the gap between the plate and a straight steel ruler. Allowable deviation: 1.5/1000L (L is the measured length).

- For angle steel bars, curvature is measured as the gap between a tensioned string connecting the two ends and the edge of the angle steel. Allowable deviation: 1/1000L (L is the measured length).

- Allowable ovality of drilled holes: ≤ 0.6 to 1 mm.

- Allowable dimensional deviations for length and width of components, as well as the center-to-center distance of holes, are taken from Table 2:

Table 2: Permissible tolerances for components

| Dimensional range in meters | Permissible dimensional tolerance relative to design ± mm |  |  |
| --- | --- | --- | --- |
|  | Length and width dimensions | Hole center-to-center distance |  |
|  |  | Sides of the hole | Adjacent holes |
| From 0.006 to 0.003 From 0.03 to 0.12 From 0.12 to 0.135 From 0.135 to 1.0 From 1.0 to 1.5 From 1.5 to 2.5 From 2.5 to 4.5 From 4.5 to 9.0 From 9.0 to 15 From 15 to 21 | ≤ 0.2 ≤ 0.3 0.5 0.8 1.5 2.0 2.5 3.0 3.5 4.0 | 0.2 0.3 0.5 0.7 1.0 1.0 1.5 2.0 2.5 4.0 | ≤ 0.2 ≤ 0.3 -0.7 -0.7 -1.0 -1.0 -1.0 -1.0 -1.0 -1.0 |

b11. Technical requirements for Tower painting

- In accordance with Government Decree No. 14/2014/ND-CP, all towers taller than 80m are painted and fitted with aviation warning lights.

- Tower marking painting shall be applied on both inner and outer surfaces of tower members after full assembly or painted on each member prior to assembly.

- The primer and topcoat are made of alkyd paint for both the inside and outside surfaces of the column.

- Steel tower painting is applied according to TCVN 8789:2011 "Protective coatings for steel structures - Technical requirements and test methods"; TCVN 8790:2011 "Protective coatings for steel structures - Execution and acceptance procedures"; and TCVN 9276:2012 "Protective coatings for steel structures - Guidance for inspection and quality control during execution ".

- The execution of steel structure painting shall include the following steps:

- The Contractor shall prepare a painting execution plan (materials preparation, surface cleaning, painting layers application, acceptance and handover).

- Supervision and inspection of execution process.

- Paint materials shall be organic solvent-based, meeting the technical requirements of the design and complying with the manufacturer’s declared standards.

- The selection of paint type, color, number of layers, thickness of each layer, surface preparation level, and maintenance/ touch-up cycle during operation shall follow the design. If no design is available, agreement between Contractor and Employer is required via the execution plan.

- Painting of steel structures shall only proceed after mechanical inspection acceptance of the structure.

* Surface preparation before painting.

- All steel surfaces shall undergo surface cleaning before painting, including removal of oil, grease, dust, mill scale, rust, welding flux, slag, and old paint (if repairing, maintaining, or touching up existing coatings)

- Surface rust level before cleaning shall be classified into four grades (A, B, C, D) as specified in Table 3. This classification shall be used for visual inspection according to ISO 8501-1:1988.

Table 3 - Rust level of the surface before cleaning

| Rust Level | Surface condition |
| --- | --- |
| A | No initial rust (surface is galvanized). |
| B | Steel surface has begun to show rust spots; rust may flake off. |
| C | Steel surface has loose or removable rust scale; small visible pitting appears. |
| D | Steel surface has extensive flaking rust; many small pits clearly visible to the naked eye. |

The rust level of the surface shall comply with level A.

- The cleanliness of the surface is classified into four levels (Sa1, Sa2, Sa2.5, Sa3) as specified in Table 4.

Table 4 – Steel Surface Cleanliness Levels Before Painting

| Cleanliness level | Corresponding surface condition |
| --- | --- |
| Sa1 | Surface cleaned of oil, grease, dust, steel scale, rust, paint, and loose contaminants; remove zinc burrs, lumps, drips, and chemicals. |
| Sa2 | Surface is mostly cleaned of oil, grease, dust, steel scale, rust, paint, and contaminants; remaining contamination tightly adheres to the surface. |
| Sa2.5 | Surface cleaned of oil, grease, dust, steel scale, rust, paint, and other impurities; remaining contamination is minimal, appearing as small spots or streaks. |
| Sa3 | Surface completely free of oil, grease, dust, steel scale, rust, paint, and other impurities; the entire surface has a uniform metallic shine. |

The required surface cleanliness level is specified as Sa1.

- After cleaning, regardless of the method used, compressed air or clean cloth must be used to completely remove dust, remaining abrasive particles, and to dry the surface.

- Acceptance inspection of surface cleaning shall be carried out according to Section 2.2.8.a.

- Painting must be performed immediately after the steel surface has passed the cleanliness inspection to prevent re-rusting or contamination from dust, oil, etc. The allowable waiting time before applying protective paint on the cleaned surface is as follows:

- Not more than 4 hours if the ambient humidity in the area is below 60%.

- Not more than 3 hours if the ambient humidity is from 60% up to 75%.

- Not more than 2 hours if the ambient humidity is from 75% to 85%

- Before painting, if the surface shows any discoloration or rust, it must be re-cleaned until it meets the requirements before proceeding with painting.

* Painting execution.

- All paints used must have full product markings, including the product code, manufacturer’s name, production date, expiration date, accompanying quality certificates, and must meet the technical requirements specified in the design.

- Upon receipt of paints for execution, the contractor must ensure full and complete acceptance of all types as specified in the design or by the Employer.

- All paints must come with usage instructions, and the contractor must strictly follow the manufacturer’s instructions for each type of paint.

- Paints must be stored in well-ventilated areas, avoiding direct sunlight or other heat sources.

- All equipment, tools, and application means must be adequately prepared and meet technical requirements.

- The painting workload must be planned and arranged to complete before breaks; unfinished work must not carry over to the next day or extend into evening with insufficient lighting.

- Painting shall only be carried out under the following conditions:

+ Only when the weather is dry, without fog, relative humidity does not exceed 85%, temperature suitable for the paint type (not higher than 50°C and not lower than 5°C), and the surface temperature must be at least 3°C above the surrounding air dew point.

+ Painting shall not be performed when rain is imminent, during rain, immediately after rain, or in windy locations

- Paint must be thoroughly stirred before use. For single-component paints, stirring can be manual but preferably with a mechanical stirrer. Stirring rods or paddles must be clean, free from oil, grease, dust, sand, or other contaminants.

- For multi-component paints, all components must be mixed thoroughly according to the manufacturer’s specified ratio. For small quantities, it is permissible to divide into portions, but care must be taken to maintain the correct ratio. Mixing must be done with a mechanical stirrer. Work must be planned to use all mixed paint within the timeframe specified by the manufacturer.

- Painting method, number of coats, and thickness per coat are specified as follows:

- Marker painting on the pole: alternate red and white segments from top to bottom: red - white - red (topmost segment painted red). Each segment’s length is specified in the column diagram drawing in the project design documents.

- Scope of tower painting: For poles 80m or taller, paint all pole segments, crossarms, including ladders. The painting scope and length of each stripe are defined in the drawings.

- Marker painting is applied to each tower section, connection plates, and ladders at the factory.

- Painted area is calculated as the total surface area of all components, without subtracting hidden parts.

- The Contractor shall paint the tower according to the design drawings.

- Pole bracing members: Do not apply primer or topcoat at bolted connections with the main members; the remaining areas are painted after pole erection.

- Main members, splice plates, and connection plates: Do not apply primer or topcoat at bolted connection points; other areas are painted after erection.

- Upper/lower members of lightning protection crossarms: Do not apply primer or topcoat around holes for lightning protection grounding.

- Pole base, top, and lightning protection members at the top: apply primer and topcoat after pole erection.

- After pole erection, paint any unpainted surfaces and areas damaged during transport or erection.

- Number of coats: Marker painting on galvanized steel poles is applied in 3 layers—primer (1 layer), first color coat, second color coat.

- Primer: The primer must be a bonding type suitable for galvanized steel surfaces. The primer layer must be dry and free of dust using organic solvent and clean cloth. Allow the surface to dry before applying subsequent coats. Apply one primer coat with dry thickness 8–12 μm. Paint quantity should be calculated to ensure uniform coverage. Minimum drying time before the next coat: 1 hour; maximum: 22 hours. Mixed primer must be used immediately within 6 hours.

- Topcolor coats: Outer color must match the requirements of the Bidding Documents (red or white), be high-quality, glossy, and color stable. Topcoat is applied over primer-coated galvanized steel. Application by airless spray or spray with compressed air; finishing on site may use brush or roller. Waiting time between coats: 1.5–2 hours. Thickness per ASTM-E376, adhesion per TCVN 2097-1993. Mixed paint must be used immediately, not exceeding 3 hours. Technical specifications and application methods are provided in the manufacturer’s catalog. Coat thickness follows manufacturer recommendations.

- Bolts, nuts, and inner surfaces of bolt holes: No painting is applied.

- The painting procedure must also comply with the paint manufacturer’s recommendations.

- Paint drying method and the time before putting the painted steel surface into service must follow the paint supplier’s instructions.

- Painting work must be closely supervised for each coat: Coats must be smooth, uniform, fully cover the surface, without pinholes, cracks, scratches, lumps, runs, or peeling. The dry film thickness of each coat must be at least 80% and at most 120% of the specified requirement. Any defects must be repaired before applying the next coat under the guidance of the technical staff.

- Hidden areas and surface defects must be touch-painted beforehand.

- For steel structures fabricated in the factory and then assembled on site, painting must also follow the regulations specified in TCXDVN 170:2007.

- Inspection after each coat and of the entire painting work must be carried out as instructed in the “Inspection and Acceptance” section for painting work.

* Inspection and acceptance

Inspect and approve the surface cleaning work.

- Inspection of grease and oil removal: The inspection of grease and oil removal shall be carried out at approximately 2÷3 points per m² and over about 40÷50% of the cleaned surface area. The procedure is as follows: Place a few drops of clean gasoline on any selected point of the surface to be inspected. After about 10÷15 seconds, use a new piece of filter paper to absorb the remaining gasoline on the tested steel surface. Take another filter paper of the same type and place a few drops of clean gasoline onto it. Allow both gasoline stains on the two filter papers to dry, then visually compare their colors. If the colors are identical, the surface shall be considered free from grease and oil.

- Dust adhesion inspection: Dust inspection shall be performed over the entire cleaned steel surface by using a magnifying glass with a magnification of 6× or higher. If no dust particles are observed, the surface is acceptable.

- Cleanliness level inspection:

- The cleanliness level shall be checked over the entire cleaned steel surface by visual inspection or with a magnifying glass, in accordance with the levels described in Table 4.

- Alternatively, inspection may be carried out by comparison with the standard reference photographs in ISO 8501-1:1988.

- Inspection may also be performed using reference samples prepared before surface cleaning begins. The Contractor and the Employer shall produce a sample with the required cleanliness level, preserve it with a transparent protective coating, and use it later as a comparison standard during inspection.

- Inspection method: Where agreed between the Employer and the Contractor, a quick surface cleanliness check may be conducted by wiping the inspected surface with a clean, dry white cotton cloth and observing the cloth. If the cloth becomes dirty, the surface cleanliness is insufficient; if the cloth becomes wet, the surface is still contaminated with oil or has not fully dried.

Inspection of painting works and coating film quality.

- Inspection of painting film defects: Inspection of painting film defects after each layer and after completion of painting shall be carried out over the entire painted area by visual examination or using a magnifying glass.

- Painting thickness inspection: The thickness of all paint coats shall be visually checked and measured using a magnetic thickness gauge. The coating thickness shall comply with the paint manufacturer’s specifications.

- Additional painting film tests: Depending on the requirements, other technical properties of the painting film may be selected for inspection in accordance with the following standards:

- TCVN 2102:1993 – Paints – Method for determination of color.

- TCVN 2097:1993 – Paints – Cutting method for determining film adhesion.

- Check the thickness of wet and dry paint layers using a specialized thickness gauge.

* Painting inspection and acceptance report

- The complete painting work acceptance report includes the following documents:

- The paint receipt record should include date of delivery, quantity, type of paint, labeling, quality confirmation certificate, usage instructions, and the names and signatures of the person delivering and receiving the paint.

- Minutes of inspection of construction equipment, tools, and installation facilities.

- Acceptance record for surface preparation/cleaning works.

- Acceptance record for painting/coating works.

- Construction logbook is maintained by the Contractor and technical supervisor.

c. Requirements for factory trial assembly of the tower.

The Contractor may propose a method for inspection and trial assembly of a sample tower in accordance with the Contractor’s Fabrication Procedure, ensuring the quality of the steel tower meets the design and Contract requirements, with no errors affecting the project schedule, and in compliance with applicable regulations and standards, or by reference to the following:

- For towers fabricated as single units, the Contractor shall carry out trial assembly for each tower. For mass-produced towers, the Contractor shall perform trial assembly of the first tower.

- The tower shall be assembled on a horizontal plane. The Contractor shall prepare a support layout to ensure the tower is positioned horizontally during trial assembly. The transmission line tower assembled at the workshop shall use the same tower members, bolts, nuts, and spring washers tightened to the required torque, as will be applied during field erection.

- The permissible misalignment of bolt holes during assembly of components into tower sections shall be in accordance with Table 5.

Table 5:

| Tolerance (mm) | Allowable tolerance In the tower segment |
| --- | --- |
| Up to 0.5 From 0.5 to 1.0 From 1.0 to 1.5 | Without limitation 50% 10% |

- The permissible tolerances for inspection of the tower during trial assembly at the fabrication workshop shall be as specified in Table 6:

Table 6:

| Name of the tolerance | Tolerance value |
| --- | --- |
| The curvature of leg members, bracing members, and horizontal members shall be measured as the maximum distance between the straight line connecting the two ends of the member and the actual curved profile of the member. | 1/750 L (L is the length of the members) but not more than 20mm |
| The curvature of the cross-arm | 1/300 L (L is the length of the cross-arm) |
| The out-of-straightness (kink) of the tower shall be measured as the maximum distance between the straight line connecting the center of the tower top and the curve representing the centerline of the tower section. | 1/750 H (H is the height of the tower) |
| The deviation of the crossarm relative to the tower base plane, when the crossarm length is: |  |
| Up to 12m | 1/150 L (L is the length of the cross-arm) |
| Greater than 15m | 1/250 L |
| The perpendicularity deviation of the tower axis relative to the tower base plane (the plane formed by the four tower legs) shall be measured as the distance between the tower centerline and the line perpendicular to the base plane passing through the center of the tower base and the tower top. | 1/750 H (H is the height of the tower) |
| The deviation of the crossarm axis from the plane passing through the tower centerline and perpendicular to the two side edges of the tower base footprint shall be measured as the displacement of the crossarm end relative to that plane. | 50mm |

- The torque value for tightening bolts during column assembly is taken as follows: According to Section b9.

- Acceptance quantity: The acceptance quantity shall be the weight of the finished product after complete fabrication (net of cut-offs, beveling, chamfering, and hole punching) for the entire tower, serving as the basis for contract payment and final settlement between the Parties. The Contractor shall prepare the As-built documentation upon acceptance of the sample tower and shall supply full quantities of bolts, nuts, and washers, ensuring sufficient fasteners for all tower connections. The final confirmed quantity of tower bolts is included in the bid price and shall not be subject to additional payment or variation.

      - Testing equipments and tools:

- Common length measuring instruments, conduit tubes, positioning devices… all testing equipment and tools must be in working order and accurate. The Contractor must provide all necessary equipment, tools, and jigs for inspection.

      - Inspection parameters:

- Curvature of leg members, bracing members, cross arm members, etc.: The curvature shall be defined as the maximum distance between the straight line connecting the two ends of the member centerline and the actual member centerline. Permissible curvature: e ≤ 1/750 L, but not exceeding 20 mm (L is the member length).

- Curvature of crossarms: The curvature shall be the distance between the straight line connecting the two ends of the crossarm and the actual curved profile of the crossarm.
Permissible deviation: e ≤ 1/300 L.

- Kink (out-of-straightness) of the tower: The kink of the tower shall be measured as the maximum distance between the straight line connecting the center of the tower top and the center of the tower base plane and the centers of the tower cross-sections along the tower body. Permissible deviation: e ≤ 1/750 H (H is the tower height).

- Method of execution: Straightness shall be checked using visual sighting methods or by instrument surveying.

- Tower base planes

- Determination of the center point of the tower base

- For sighting inspection, small wooden blocks (20 × 20 × 10 mm) shall be fixed at the center of the planes of each tower segment. The centers of the tower top and the tower base shall be sighted and compared with the center points of the intermediate tower segments. The use of an optical instrument provides higher accuracy.

- A plumb bob shall be used to determine longitudinal kink (out-of-straightness) along the tower line.

- The perpendicularity deviation of the tower axis relative to the tower base plane shall be measured as the offset between the tower centerline and the line perpendicular to the base plane passing through the center of the tower base and the tower top. Permissible deviation: e ≤ 1/750 H (H is the tower height).

- The centerline of the crossarm axis shall coincide with the plane formed by the tower axis and the line originating from the center of the base and perpendicular to the side edge of the tower base footprint. Any deviation of the crossarm centerline from this plane shall be measured as the displacement of the crossarm end.
Permissible deviation: e ≤ 50 mm.

- The Contractor shall carry out tower trial assembly in accordance with EVN Decision No. 428/QĐ-EVN dated 26 March 2025 and the standards TCVN 12002:2020, TCVN 13194:2020, and TCXDVN 170:2007. Where required by the competent authority, the Employer may decide to inspect or waive inspection of the Contractor’s trial erection (the accommodation and travel expenses for the inspection team shall be borne by the Employer). The Employer’s inspection shall not relieve the Contractor/manufacturer of responsibility for the quality of the towers supplied under this package.

d. Acceptance Requirements

d.1 Acceptance procedure

- Step 1: Incoming material inspection (internal acceptance) performed by the Contractor

- Incoming materials shall be inspected for quantity, quality, specifications, grades/types, and quality certificates in accordance with the Contract requirements.

- The Contractor shall take at least 10 (ten) random steel material samples for testing at an independent domestic testing laboratory. Witnessing parties for sampling shall include the Employer/Buyer, the Design consultant, and the Contractor (all accommodation and travel expenses for the sampling delegation shall be borne by the Contractor). The testing laboratory shall be submitted by the Contractor to the Employer for review and approval prior to sampling of incoming materials. Sampling and testing costs are deemed included in the Contract price.

- Where delivery or supply of incoming materials is made in multiple batches, sampling and testing shall be organized in corresponding batches for each delivery/material inspection lot.

- Step 2: Inspection of products after cold fabrication (internal acceptance), performed by the Contractor.

- Step 3: Inspection of products after hot-dip galvanizing (internal acceptance), performed by the Contractor, and sampling of finished products at the fabrication workshop with the participation of the Employer/Buyer, the Contractor, and the design consultant (all accommodation and travel expenses for the sampling delegation shall be borne by the Contractor).

- The Contractor shall take at least 10 (ten) random finished-product samples for testing to evaluate mechanical properties and galvanizing quality at an independent domestic testing laboratory. The testing laboratory shall be submitted by the Contractor to the Employer for review and approval prior to sampling. Test results shall include mechanical testing, coating thickness, and coating adhesion. Sampling and testing costs are deemed included in the Contract price. Where delivery is made in multiple batches, sampling shall be organized for each corresponding batch.

- Step 4: Acceptance of completed products at site and sampling of finished products at site with the participation of the Employer/Buyer, the Contractor, and the Design Consultant.

- The Contractor shall take at least 10 (ten) random product samples for testing to evaluate mechanical properties and galvanizing quality at an independent domestic testing laboratory. The testing laboratory shall be submitted by the Contractor to the Employer for review and approval prior to sampling. Test results shall include mechanical testing, coating thickness, and coating adhesion. Sampling and testing costs are deemed included in the Contract price. Where delivery is made in multiple batches, sampling shall be organized for each corresponding batch.

      - Acceptance documents:

- Documents evidencing origin and traceability, and test certificates for incoming materials (Framework Agreement, purchase invoices, bills of lading, etc.).

- Manufacturer’s certificates confirming the quantity, quality, specifications, and grades/types of incoming materials.

- Test results issued by an independent inspection/testing body for incoming materials (steel, zinc), including mechanical properties, weld thickness, etc.

- Incoming material inspection report (internal acceptance) performed by the Contractor.

- Inspection report for cold-fabricated products after fabrication (including weld ultrasonic test results) (internal acceptance), performed by the Contractor.

- Inspection report for products after hot-dip galvanizing (including coating thickness and coating adhesion test results) (internal acceptance), performed by the Contractor.

- Test results issued by an independent inspection/testing body for completed products (including mechanical properties, galvanizing, etc.).

- Acceptance record for completed products at site with the participation of the Buyer, the Contractor/Supplier, and the Design Consultant.

- Other documents as specified in Section VII of the Bidding Documents.

- For payment procedures, the Manufacturer shall submit 05 sets of As-built drawings after fabrication for each tower type. The documentation shall include complete material records, steel quality certificates, steel tensile test samples, base-plate weld ultrasonic test results, galvanizing thickness measurements, tower fabrication acceptance records, and factory release certificates as specified above.

- As-built drawings after fabrication shall fully list the actual dimensional parameters of the tower, including: general assembly drawings; detailed drawings of all tower components; material take-off schedules indicating types of structural sections/plates/bolts, quantities, and fabrication weights of each component and the total weight. The total weight shall include:

  - Black-steel weight (members and plates) prior to deduction for bevel cutting and bolt holes;

  - Weight of connection bolts (including bolts, washers, and nuts in full set);

  - Total tower weight prior to deduction for bevel cutting and bolt holes (before galvanizing);

  - Total tower weight after deduction for bevel cutting and bolt holes (before galvanizing);

  - Total tower weight after deduction for bevel cutting and bolt holes (after galvanizing).

- All the above documents shall be digitized by the Contractor in accordance with the Buyer’s instructions, and all digitized data files shall be provided to the Buyer.

d.2 Execution arrangements

- The parties participating in the acceptance of completed products at site shall include representatives of the Employer (if any), the Design Consultant (if any), the Manufacturer, and the Buyer (PC Contractor). After each inspection and acceptance, an inspection and acceptance record shall be prepared.

- Prior to organizing the acceptance of completed products at site, the Manufacturer or the Buyer shall prepare and submit a complete set of documentation and relevant certificates in accordance with the requirements for acceptance of the completed products (documents evidencing origin and traceability; quantity and quality of incoming materials; steel quality certificates; base-plate weld ultrasonic test results; galvanizing thickness measurements; etc.).

- The Contractor shall notify the Buyer at least 07 days in advance of the schedule for witnessing sampling and acceptance tests in order to coordinate with the relevant parties. All costs for the Buyer’s acceptance/inspection delegation (air tickets, transportation, accommodation, etc. during each acceptance visit) shall be borne by the Contractor.

e. Tower Acceptance Requirements

In the event that any tower delivered for erection at site does not meet the specified requirements, the tower supplier/manufacturer shall carry out corrective actions for each affected tower type to achieve compliance with the technical requirements within a period not exceeding 07 days from the date of receipt of the Employer’s notification. All related costs (including transportation, re-fabrication/repair, materials required for rectification, and all inspection and re-acceptance costs until compliance is achieved, etc.) shall be borne by the tower manufacturer/supplier and shall not be included in the Contract price.

f. Acceptance and Payment

- Measuring units: kg

- Quantity: The quantity shall be the weight of black steel used for fabrication of the tower (excluding the weight of bolts and nuts and excluding galvanizing weight), after deduction for bevel cutting and bolt holes, measured based on actual as-built quantities in accordance with the approved design and technical requirements.

- Unit rate composition: The unit rate shall include all costs necessary to complete 01 kg of finished black steel, including but not limited to the following: preparation of method statements; preparation of as-built drawings after fabrication; costs of materials, fabrication, manufacturing, and transportation to site; testing, measurement, and sampling; costs of replacement of steel members that must be re-fabricated due to sampling; labor costs; equipment costs; and all related costs for fabrication, welding, and assembly into components/equipment in accordance with the fabrication drawings and the approved procedures and technical requirements.

- It shall also include costs for dimensional inspection during fabrication; trial assembly of the template tower; surface preparation; galvanizing; finished-product testing; finishing, packing, and marking/numbering of components; and all other costs required to meet the technical requirements of the Contract.

g. Packaging requirements

- Packing and delivery shall comply with TCVN 128-63.

- All components of each tower shall be packed together in accordance with the packing list for each shipment (unless otherwise instructed). Packages shall be prepared per tower, and identical components shall be bundled together in the same package to facilitate transportation, handling, and subsequent erection.

- Packing methods:

  - Bundles: Relatively large components shall be bundled such that the weight of each bundle does not exceed 2000 kg. Each bundle shall be securely fastened with steel strapping; to prevent damage to the galvanizing coating, soft padding shall be placed beneath the straps.

  - Crates: All small components such as bolts, nuts, washers, splice plates, and other small items shall be packed in wooden crates. Bolts, nuts, and washers shall first be packed into woven plastic or burlap bags before being placed into the wooden crates. The weight of each wooden crate shall not exceed 500 kg.

- The packing layout/packing plan shall be submitted to the Employer one week prior to delivery.

- Each tower shall be supplied in numbered and clearly labeled packages. Packages shall be sufficiently strong and secure to allow lifting and handling by crane. Each package shall include a packing list indicating components and quantities, together with a package list for complete assembly of one tower.

- Bolts, nuts, and washers of different diameters and lengths shall be sorted and packed separately in different fabric bags and packages.

h. Shipping requirements

When transporting towers, follow the manufacturer's instructions. The packages must be securely fastened with ropes to prevent shaking or shifting during transport, and safety measures must be taken during transit.

Section 2.3. OTHER REQUIREMENTS

Based on the Decision approving the overall construction schedule of the project, the delivery schedule will be negotiated during the contract negotiation, finalization, and execution process.

The Contractor must submit the following documents in the Bidding documents:

- Written commitment on the operational service life for each type of equipment.

- Written commitment on the defect and failure rate (probability) for each type of equipment, together with a commitment to mobilize to site to investigate and determine the causes of defects, failures, or incidents, and to implement remedial measures if such defects or failures are attributable to the Manufacturer, upon the Employer’s request.

### 3. DRAWINGS

(Refer to Design drawings)