### SECTION 2.1

### TECHNICAL SPECIFICATIONS AND DATA SHEETS OF SUBSTATION

TABLE OF CONTENTS

Chapter 1	TECHNICAL SPECIFICATIONS	7

1.	TECHNICAL SPECIFICATIONS	7

1.1.	GENERAL TECHNICAL REQUIREMENTS	7

1.1.1.	General System Data And Environmental Conditions	7

1.1.2.	Data for all Equipment under Contract	8

1.1.3.	Design	8

1.1.4.	Supplier’s Communications, Drawings, Data and Instructions	9

1.1.5.	System of Measurement	12

1.1.6.	Tests and Inspection	12

1.1.7.	Materials	15

1.1.8.	Workmanship	15

1.1.9.	Electric Welding	16

1.1.10.	Provisions for Erection and Installation	16

1.1.11.	Standards	16

1.1.12.	Designation of Trade Name or Catalogue Name and Number	17

1.1.13.	Tropical Serviceability	17

1.1.14.	Performance under Site Environmental Conditions	18

1.1.15.	Cleanliness	19

1.1.16.	Surface Treatment and Corrosion Protection	19

1.1.17.	Painting	20

1.1.18.	Preparation for Shipment and Storage	21

1.1.19.	Equipment Designation (Equipment Marking)	22

1.1.20.	Interchange ability and Standardization of Small Equipment	23

1.1.21.	Spare Parts	24

1.1.22.	Quality Assurance Requirements	24

2.	DESCRIPTION OF EQUIPMENT AND MATERIALSFOR SUBSTATION	29

2.1.	CIRCUIT BREAKERS	29

2.1.1.	220kV Circuit breaker, 110kV Circuit breaker	29

2.1.2.	22kV Circuit Breaker	37

2.2.	DISCONNECTOR AND EARTHING SWWITCH	41

2.2.1.	220kV and 110kV Disconnectors and Earthing Switches	41

2.2.2.	22kV Disconnector and Earthing Switch	49

2.3.	CURRENT TRANSFORMER	52

2.3.1.	220kV Current Transformers	52

2.3.2.	110kV Current Transformer	57

2.3.3.	22kV Current Transformer	59

2.4.	VOLTAGE TRANSFORMER	61

2.4.1.	220kV Capacitor voltage transformer	61

2.4.2.	110kV Capacitor Voltage Transformer	66

2.4.3.	22kV Voltage transformer	69

2.5.	SURGE ARRESTER	71

2.5.1.	220kV Surge Arrester	71

2.5.2.	110kV, 22kV Surge Arrester	79

2.6.	CAPACITOR	81

2.7.	POST INSULATOR	87

2.8.	INSULATOR STRINGS	91

2.9.	FITTINGS	96

2.10.	TUBE, CONDUCTORS AND FITTINGS	104

2.11.	HV TERMINAL CONNECTOR	108

2.11.1	General requirements	108

2.11.2	Contact grease	108

2.11.3	Type Test	108

2.11.4	Document	109

2.12.	SUPPORT STRUCTURES FOR EQUIPMENT	109

2.13.	DATA AND DOCUMENTATION REQUIREMENTS	111

2.13.1	General	111

2.13.2	Data and Information to be submitted with the Bid	111

2.14.	PACKING, SHIPPING AND TRANSPORT	113

2.15.	REQUIRED FOR LIST OF TYPE TEST REPORT	113

Chapter 2	DATA SHEETS	115

I. DATA SHEET FOR SUBSTATION	116

1.	CIRCUIT BREAKERS	116

1.1.	220kV Circuit Breaker	116

1.2.	110kV Circuit Breaker	121

1.3.	22kV Circuit Breaker	126

2.	DISCONNECTOR AND EARTHING SWWITCH	130

2.1.	220kV Disconnector and Earthing switch	130

2.2.	110kV Disconnector and Earthing switch	134

22kV Disconnector and Earthing switch	138

3.	CURRENT TRANSFORMER	141

3.1.	220kV Current Transformer	141

3.2.	110kV Current Transformer	143

3.3.	22kV Current Transformer	146

4.	VOLTAGE TRANSFORMER	150

4.1.	220kV Capacitor Voltage Transformer	150

4.2.	110kV Capacitor Voltage Transformer	153

4.3.	22kV Voltage Transformer	156

5.	SURGE ARRESTER	159

5.1.	220kV Surge Arrester	159

5.2.	110kV Surge Arrester	162

5.3.	22kV Surge Arrester	164

6.	110KV CAPACITOR	167

7.	POST INSULATOR	173

7.1.	220kV Post Insulator	173

7.2.	110kV Post Insulator	175

7.3.	22KV POST INSULATOR	177

8.	INSULATOR STRINGS	179

8.1.	220kV Suspension and Tension Insulator	179

8.2.	110kV Suspension and Tension Insulator	181

9.	TUBE AND CONDUCTOR	183

9.1.	ALUMINUM TUBE Ф160/144	183

9.2.	ALUMINUM TUBE Ф120/108	183

9.3.	AAC-630	184

9.4.	ACSR-185/29-XLPE/HDPE	186

10.	HV CONNECTOR	186

SECTION 2.1. TECHNICAL SPECIFICATIONS AND DATA SHEETS of SUBSTATION

- TECHNICAL SPECIFICATIONS

    - TECHNICAL SPECIFICATIONS

      - GENERAL TECHNICAL REQUIREMENTS

- This Section specifies the applicable requirements to calculations, drawings, equipment, inspection, tests, materials, working stresses, workmanship and standards involved in the design and manufacture of the works and supplies under the project. Further requirements of a special nature are contained in subsequent sections, i.e. the Technical Data Sheets and the Drawings. In the following, the words "Supplier" and "Contractor" shall be considered to have the same meaning.

    - General System Data And Environmental Conditions

- The main electrical system data of EVN's electric power network in which the equipment and materials under contract shall operate satisfactorily and without derating, are as follows:

| System Voltage (nominal) | 220kV | 110kV | 22kV |
| --- | --- | --- | --- |
| Max. continuous system voltage | 245kV | 121kV | 24kV |
| System Frequency | 50Hz | 50Hz | 50Hz |
| Short circuit level | 50kA/1s | 40kA/1s | 25kA/1s |
| Lighting impulse withstand voltage, kVpeak | 1050kV | 550kV | 125kV |
| Short-time power-frequency voltage for voltage transformer, kVrms | 460kV | 230kV | 50kV |
| CT Secondary | 1A | 1A | 1A |
| VT Secondary | 110V | 110V | 110V |
| Auxiliary Voltage | 220VDC 380/220VAC | 220VDC 380/220VAC | 220VDC 380/220VAC |

- All equipment and installations under the project shall operate without restriction, deterioration or derating and in the accordance with Supplier's guarantees under the following environmental conditions encountered at the Substation locations:

- Climatic condition			: Tropical

- Average air temperature		: 25°C

- Minimum air temperature:		: 0°C

- Maximum air temperature		: 45°C

- Average humidity			: 85%

- Maximum humidity		: 100%

- Maximum wind   			: 160km/h

- Altitude above sea level		: ≤ 1000 m

- Seismic factor			: 0,15g

- Pollution level			: Heavy

- Equipment tropicalization required

    - Data for all Equipment under Contract

- In addition to matching the general system data and environmental conditions, the following data as applicable shall be met by all equipment supplied under the Contract, except where otherwise stated or modified in the more specialized sections of these Bidding Documents.

220kV system:

| Rated voltage | : | 245kV |
| --- | --- | --- |
| Lightning impulse withstand voltage | : | 1050kV |
| Power frequency withstand voltage | : | 460kV |
| Short time current (1 sec) | : | 50kA |
| Creepage distance of insulators | : | min. 31mm/kV |
| Protection class | : | IP55 |

110kV system:

| Rated voltage | : | 123kV |
| --- | --- | --- |
| Lightning impulse withstand voltage | : | 550kV |
| Power frequency withstand voltage | : | 230kV |
| Short time current (1 sec) | : | 40kA |
| Creepage distance of insulators | : | min. 31mm/kV |
| Protection class | : | IP55 |

22kV system:

| Rated voltage | : | 24kV |
| --- | --- | --- |
| Lightning impulse withstand voltage | : | 125kV |
| Power frequency withstand voltage | : | 50kV |
| Short time current (1 sec) | : | 25kA |
| Creepage distance of insulators | : | min. 31mm/kV |
| Protection class | : | IP55 |

    - Design

- The Contractor shall perform all necessary calculations to ensure the full functionality and proper interaction, including e.g. calculations to verify adequacy of the static strength of supports and pedestals, sags and tensions of conductors, sufficiency of CT ratings for proper functioning of protection etc.

- The Contractor shall provide complete bills of quantity for all material and equipment which ensure completeness of supply in every respect for the purpose of fully functional installations. Where he finds that necessary quantities deviate from the quantities set forth in Clause I.  List of goods and related services (in this section), this shall be pointed out by him in order to decide whether a variation will have to be effected.

    - Supplier’s Communications, Drawings, Data and Instructions

- The Supplier shall, besides normal communication, submit for approval drawings, design data, installation, operating and maintenance instructions, and catalogue cuts as outlined herein. The sequence of submission shall be such that sufficient previous information is available for checking each document when it is received.

      - Document to be prepared by Supplier

- The general documents, calculations, certifications, manuals, drawings, ect. relating to the manufacturing works, which are to be prepared during detailed design by the Supplier are lists here below. The Supplier’s attention is drawn to various other chapters of the Bidding Documents, where detailed contents of documentation are specified.

- Outline drawings

- The Supplier shall, within forty-five (45) calendar days after Effective Day of Contract, submit outline drawings of the equipment to be furnished under the Contract, together with weights, external forces, anchoring details and sufficient overall dimensions to facilitate preparation of final designs of the structural foundations.

- Diagrams

- Logic, schematic, circuit and wiring diagrams including list of materials, cable lists, etc. shall also be submitted by the Supplier.

- These diagrams shall show the internal and external connections of all apparatus, their designations, terminal numbers, color codes, ect. and shall be used for manufacturing, installation and operation of the equipment.

- Arrangement drawings

- Arrangement drawings shall be prepared by the Supplier, which show the location and interconnections of equipment and materials under Contract, and their integration into the existing installations.

- Detailed drawings, designs and specifications:

- Before proceeding with the manufacture of equipment, the Supplier shall submit corresponding detailed drawings, designs and detailed specifications (in typewritten hardbound form) which shall show all details of materials, manufacture, assembly, testing, erection, commissioning, operation and maintenance of the equipment in comformity with the Contract requirements.

- The detailed drawings and specification shall include, but not necessarily be limited to the following:

- Switchyard layout, Single line diagrams, diameter-sections,… drawings;

- General assembly drawings;

- Assembly drawings, showing:

- Sectional views

- Details of mounting of the internal equipment

- Function of the assemblies

- Adjustment and operating ranges

- Concrete pedestals and foundation bolts and anchors

- Field tolerance

- All field joints

- Methods of  lubrication (if required)

- Detail manufacturing drawings, showing:

- Detail dimensions

- Tolerances

- Materials

- Nameplate diagrams

- Manufacturing

- Fabrication

- Painting, including final color scheme

- Heat treatment

- Welding

- Surface treatment

- Testing

- Designs computation and final design data

- After the Supplier has completed the preliminary design of the equipment, he shall submit the final design data, design analysis and design computation (referred to as designs) along with all other specified designs and study, all typewritten and in book form, clearly laid out with all the design criteria and standards indicated.

- Parts bills

- The Supplier shall submit with the first drawing issue, where applicable, corresponding parts bills. Reference to the respective detail or assembly drawing, materials used or catalogues shall be made.

- Catalogue cuts, illustrations, ect.

- Applicable requirements of this paragraph with reference to drawings shall apply equally to catalogue cuts, illustrations, printed specifications, designs data, analysis and calculation, and manufacturer’s discriptive literature and instructions for all equipment furnished to demonstrate fully that all parts will conform to the requirements and intent of the Contract Documents.

- Installation manual

- The Supplier shall provide the Purchaser with an Installation Manual covering installation procedures and instructions to facilitate smooth erection, assembly and testing on site of all equipment to be installed.

- The instructions therein shall specify the exact procedures to be followed during installation, indicate data to be measured and recorded (adjustments, setting of limits, ect.), quantities, dimentions, and tolerances to be checked, ect.

- The manual shall include information on handling and slinging the major pieces of equipment, erection, tolerances, setting and adjustments and special precautions to be taken during installation

- The Supplier shall submit six (6) copies each of the Installation Manual for each equipment per substation per schedule to the Purchaser.

- Commission manual

- The Supplier shall provide the Purchaser with a Commission Manual, which shall be similar in size and form to the Installation Manual and shall include procedures and instructions to be followed during the commission of all equipment to be installed.

- The instructions there in shall specify the exact procedures to be followed during commission, and shall indicate all data to be measured (and where appropriate, recorded in the manual itself) and all adjustments, setting of limits, ect., quantities, dimensions, and tolerances to be checked.

- The Supplier shall submit six (6) copies each of the Commission Manual for each equipment per substation per schedule to the Purchaser.

- Operation and maintenance manual

- The Supplier shall provide the Purchaser with an Operation and maintenance manual similar in size and form with the other manual and shall include procedures and instructions to be followed by the operating and maintenance staff necessary for reliable operating and maintenance the equipment.

- The manual shall contain at least the following documents and data:

- General description of the equipment, operation in particular

- Main technical characteristics

- Connection to the external system

- Instructions for operating personnel including periodic tests, check-points, actions required following each individual alarm signal, etc.

- Summary of important rules, standards, safety precautions and instruction to be followed during equipment operation and maintenance.

- Safety and warning signs to be placed in the plant/ substation, etc.

- Enclosures: Important principle diagrams and layout diagrams.

- Section on “maintenance” shall be divided into two parts, namely:

- Current (preventive) maintenance indicating inspection periods, routine cleaning and lubricating procedures (if required), safety checks, adjustments, etc.

- Repairs and overhauls describing the dismantling, removal and replacement of part (with spare parts), trouble shooting guides, repair instruction, etc.

- The Operation and Maintenance Manual, supplemented by any additional drawings and project documents to be submitted to the Purchaser will be the only document to be generally used by the Operating staff.

- The Supplier shall submit six (6) copies each of the Operation and Maintenance Manual for each equipment per substation per schedule to the Purchaser.

      - Processing of  drawings

- Drawings and documents as mentioned above shall be submitted to the Purchaser for review.

- All documents to Purchaser shall meet the following requirements:

- They shall be marked with a document identification number, issue date and revision status;

- They shall be submitted in at least five (5) copies printed with dark lines/ letters in light durable paper.

- All drawings, calculation sheets, etc. shall be folded down to A4 size (210 x 297 mm), A3 (420 x 297 mm) or a similar standard size acceptable to the Purchaser.

- Award of Contract does not imply approval of drawings and submitted by the Supplier with his bid.

- The Supplier shall send all drawings, specifications and designs attached with all supporting information to the Purchaser.

- Review of the Supplier’s drawings shall not be held to relieve the Supplier or any part of the Supplier’s obligations to meet all the requirements of this specifications nor of the responsibility for the correctness of the Supplier’s drawings.

      - Design review meeting

- The Supplier may call for design review meeting at Purchaser’s premises during the processing stage to seek the approval of the Purchaser to all design drawings, to review, clarify and evaluate the design of the Contract Specification. The Supplier shall submit a meeting agenda seven (7) days prior to the meeting. The Supplier shall furnish minutes of the design meetings within three (3) days completion of each meeting.

    - System of Measurement

- Metric units shall be used in all documents, correspondence, technical schedules and drawings. On drawings or printed pamphlets where other units have been used, the metric equivalent shall be marked in addition.

    - Tests and Inspection

      - General

- The Supplier shall provide a test specification covering all tests on Supplier’s premises. Successful completion, as deemed by the Purchaser, of Inspection and Tests on Supplier’s premises shall be a prerequisite to shipment of all materials, equipment, software or system(s). Following successful completion of inspection and tests on his premises, the Supplier shall, with the consent of the Purchaser, proceed with the delivery of the equipment, materials, software or system(s) in accordance with the Technical Specification for the equipment.

- The objective of the test specification shall be to set forth the means, manner and circumstances in which to verify compliance with the Contract requirements including all functional and operation performance claims for the material, components, equipment, software or system made by the Supplier and/or the original equipment manufacturer.

- The test specification shall include a program for Factory Acceptance Test (FAT) and detail as the followings:

- Requirements to be tested;

- Step-by-step method of testing;

- Expected results of test

- Approval of the test specification/procedure will not prejudice the Purchaser’s right to order additional tests, should the Purchaser deem, following approval but before his acceptance of the material, equipment, software of system(s) for shipment, that certain conditions or combination of conditions were not foreseen in the test specification, in order to demonstrate that performance requirements of this Specification have been met.

- Copies of the type test report with certificate issued by independent accredited testing laboratories which are accredited according to the international standard EN ISO/IEC 17025:2005. The certificate of Accreditation of the laboratory must be submitted as well.

      - Inspection on Supplier’s Premises

- The Purchaser reserves the right to inspect all shop and assembly work associated with the Works, verify quantities consigned to stores and inspect quality control and assurance records as well as shop and purchase order records. When scheduled, and as often as the Purchaser deems appropriate, progress will be monitored with respect to Key Dates in the Contract Schedule.

- The Supplier shall demonstrate and furnish evidence that general progress is being maintained so that no activities are in danger of becoming the critical path and that specific progress of those activities on the critical path meet all target dates set by the Supplier as well as Key Dates in the Contract Schedule.

- The Supplier shall furnish the Purchaser, a list of Suppliers and the components, materials, equipment or software to be furnished by them for use in the Works, in sufficient time to permit inspection and testing of all components, materials, equipment and software. Purchase Orders shall clearly indicate level of inspection to which purchased items will be subject.

- All shop orders or instructions to production and manufacturing departments shall quote the pertinent requirements of the Specification and shall bear a suitable notation advising quality control inspection requirements. A system for advising the quality control department of same shall exist.  If so requested by the Purchaser, the Supplier shall furnish triplicate copies of the designated internal orders and instructions.

- Final inspection prior to shipment shall take place following successful completion of the Factory Acceptance Tests. The Supplier shall forward to the Purchaser instructions specifying methods for dismantling, packing and crating for shipment no later than sixty (60) days prior to shipment.

      - Tests on Supplier’s Premises

- Routine Tests

- The Supplier shall perform routine tests in accordance with requirements of the Specification and the Supplier’s test specification approved by the Purchaser. The Supplier shall give the Purchaser access to Works to determine or assess compliance with the provisions of this Specification or to witness Supplier’s routine shop tests. The Supplier shall submit results of routine tests within fifteen (15) days after performance of the tests.

- Type Tests

- The Supplier shall carry out all type tests called for in this Specification and such tests in the Standard are in accordance with criteria and to the extent specified in the Specification and on custom manufactured items as called for by the Purchaser to obtain required performance data.

- Upon submission of relevant test certificates from an independent testing agency approved by the Purchaser, and proof that the equipment to be tested is identical to that covered by the test certificates, the Purchaser will waive the requirements for corresponding type tests called for in this Specification and/or specified in the Standards The Bidder should already submit with the bid type tests reports for the main equipment and accessories from independent testing agencies. Bids which will be submitted without such certificates (for the main equipment) shall be rejected.

- Factory Acceptance Tests

- Prior to shipping and final inspection, tests hereinafter referred to as Factory Acceptance Tests (FAT) shall be conducted by the Supplier at his plant and will be witnessed by the Purchaser. All cost for Purchaser’s persons participate in these FATs such as air return ticket, local transportation, accommodation, etc . . shall be the Supplier expenditure.

- The Supplier shall carry out tests, as may be required by the specified Standards and the Quality Control and Assurance Program, as well as the entire test program, approved by the Purchaser, prior to the witnessed FAT, remove all faults found and correct all failures so that to the best of his knowledge, no functional or procedural errors will occur during the witness FAT.

- At the commencement of the witness FAT, all equipment shall be brought together in one place, integrated and the configuration/set-up at the factory site shall be identical to that to be installed at the site and any equipment and software necessary for the proper operation of the equipment shall have reached its final form, not to be changed during the FAT and until commencement of commissioning at site.

- The Supplier shall immediately advise the Purchaser should failures occur, take remedial action subject to the Purchaser’s approval and proceed with the FAT as and when directed by the Purchaser. It shall be the Purchaser’s prerogative to order a repeat of all such tests that he deems may have been affected by the failure.

- The Supplier shall ensure that during the test, all hard copies from output devices are retained and no outside parties interfere in any way with testing, equipment or test instruments, fixtures and jigs for the entire duration of the FAT. Only Supplier’s personnel who are needed on the testing of the equipment shall be allowed in the test area. The Supplier shall appoint a chief-tester who shall be responsible for conducting the test, ensuring at all times that the test instruments, fixtures, jigs and extender cards, and those of the Supplier’s personnel who in any way may contribute to the test, including testers, specialists and maintenance personnel are available prior to scheduled commencement of each test or and when instructed by the Purchaser.

- The chief-tester shall also be responsible that the accurate record of tests is kept and each individual test is duly initialed and dated by the tester and marked either passed or failed with annotations of antecedents and observations concerning the test. For each day of testing, the chief-tester shall submit to the Purchaser the proposed disposition of each criterion that failed during the previous day of testing, prior to commencement of the tests scheduled for that day. Tests witnessed by the Purchaser will be initialed accordingly by him on the test record. The test record and dispositions, and any other pertinent supporting data and documents shall form part of a test report to be submitted in accordance with the specification.

- Material, equipment, software or system(s) shall be required to pass one complete run of functional tests with satisfactory results and shall have all faults and failures corrected. At completion of all tests, as well as at any time during the test at the Purchaser’s discretion, test results, except for the parts comprising dynamic data, shall be compared with the reference copy. If no differences are detected and all tests have demonstrated in compliance with the requirements of this Specification, then the FAT will be deemed successful.

- Note: Purchaser’s persons will not participate in FAT test of Eqipments at the factory. Bidder and manufacturers are responsible for FAT testing of the device and responsible for the test parameters of the device. Bidder is responsible for providing FAT test report upon delivery.

- Field Test

- Field tests and acceptance tests, if any to determine whether the requirements of the specification have been fulfilled, shall generally be performed by the Purchaser, but the Supplier shall delegate his engineer(s) for assistance in this work, as indicated in the schedule of requirements.

- Waiver of Factory Acceptance Tests Witnessing / Inspection by Purchaser

- If the Purchaser opted not to witness the Factory Acceptance Tests, Purchaser will issue a Certificate of Waiver of Tests Witnessing/Inspection for the equipment and materials. In such case, the Supplier shall proceed with the Factory Tests in accordance with the requirement of the specification and the manufacturer’s test specification as approved by the Purchaser.

- Where Factory Tests are not required to be witnessed by Purchaser’s representative(s) as indicated in the Technical Data Sheets of the equipment, a Certificate of Waiver of Tests Witnessing/ Inspection will be issued also by the Purchaser. In this case, no claim whatsoever can be made by the Purchaser on the Supplier as a result of waiving the Factory Acceptance Tests.

    - Materials

- All materials to be used under this Contract shall be new, the best of their respective kinds and free from defects and imperfections. All materials shall comply with the latest revisions or edition of the specified standards for each equipment specification unless otherwise specified or permitted by the Purchaser.

- When other standards are used, Supplier shall indicate the equivalence between the materials used and the corresponding materials following the specified standards in the equipment specification and shall obtain the approval of the Purchaser before starting the manufacture of the equipment and materials.

- Materials and finishes selected for equipment shall be suitable for the purpose intended and for the humid tropical conditions under which the equipment is to operate. The use of other materials may be permitted where the equipment is hermetically sealed.

- Iron and steel where possible, shall be avoided in instruments and in electrical relays. Instrument screws (except those forming part of magnetic circuit shall also be brass or bronze. Steel screws, when used, shall be zinc, cadmium or chromium plated, or when plating is not possible owing to tolerance limitations, shall be of corrosion-resisting steel. Springs shall be of a non-rusting material, such as phosphor-bronze or nickel silver.

- The names of manufacturers of equipment and articles contemplated for incorporation in the work together with performance capacities and other significant information pertaining to the equipment, shall be furnished for approval. Equipment and articles installed or used without such approval shall be at the risk of subsequent rejections.

Test of materials:

- Materials, parts and assemblies thereof  entering into the work shall be tested, unless otherwise directed, according to the best commercial method for particular type and class of work. When the Supplier desires to stock material not manufactured specifically for the equipment furnished, satisfactory evidence that such material conforms to the requirements herein stated shall be furnished, in which case tests on these materials may be waived. Certified mill tests reports of materials will be acceptable.

- Certified copies of test reports shall be furnished in triplicate as soon as possible after the tests are made and shall be in the manufacturer’s possession prior to incorporating that material in the work. The reports shall be in such form as to enable determining compliance with the applicable specifications for the material tested. When requested, tests shall be made in the presence of a duly authorized inspector.

    - Workmanship

- Workmanship shall be of first-class quality and in accordance with the best modern practice for the manufacture of high grade equipment, notwithstanding any omissions from these specification and drawings.

- All materials supplied under this specification shall be unused, of recent manufacture, free of defects or irregularities and the best available considering durability, strength and intended service suitability and best engineering practice.

- All parts shall conform to the dimensions shown on, and shall be built in accordance with approved drawings. The surface finish of all parts and components shall be in conformity with the respective strength, fit and service requirements.

- Like parts and spare parts shall be interchangeable whenever possible.

- Machining of renewable parts shall be accurate and to specified dimensions so that replacement of those parts fabricated or made according to dimensions to indicated in the drawings could be readily installed.

    - Electric Welding

      - Preparation of Base Material

- Members to be joined by welding shall be cut accurately to size with edges sheared, flame-cut, or machined to suit the required type of welding and to allow thorough penetration and good fusion of the weld with the base metal. The cut surfaces shall be free from all defects such as lamination, surface defects caused by shearing or flame-cut operations, or any other injurious defects. The edges to be welded shall be free from rust, oil, grease, and other foreign matter.

      - Welded Construction and Stress Relief

- All weld fabricated parts except minor parts, those where stress is not important, or those which are specifically exempted from stress relieving, shall be designed, fabricated, and inspected in accordance with the ASME Boiler and Pressure Vessel Code, Requirements for Unfired Pressure Vessels Fabricated by Welding, or an approved equivalent standard. All such parts shall be stress-relieved as a unit prior to machining. Radiographic or other non-destructive weld tests will not be required except when it is desired to make such examination as a means of judging acceptability of any weld when, in the opinion of the Purchaser, doubt exists as to their quality in which case such tests shall be made at the Supplier’s expense.

      - Acceptance of Welded Structures

- The acceptance of the welded work shall depend upon correct dimensions and alignment and absence of distortion in the structure, upon satisfactory results from the examination and testing of the joints in accordance with the instructions given on the drawings and the soundness of the welds and upon general good workmanship.

      - Cleaning

- All excess weld materials, slag, splatters and flux residues shall be removed from the steel work.

    - Provisions for Erection and Installation

- All parts of the equipment to be assembled on site must be connected by means of screws and bolts/ nuts, welding is not accepted except for accessories and where expressly stated.

- It must be possible, except in particular cases, to introduce and draw out all the indoor equipment through the doors available.

    - Standards

- Unless specified otherwise in the various sections of this technical specifications for equipment, the design, materials, manufacture and testing of all works under this Contract shall comply with the latest revision or edition of the various standards specified for each equipment section of the specification.

- The latest edition of each standard shall mean the latest edition available at the date of latest submission of Bids.

- Equipment or materials meeting other internationally accepted standards, which ensure en equal or higher quality than the standards mentioned, will also be accepted.

- In case of any apparent conflict among standards, codes or this specification, the Supplier shall refer the conflict to Purchaser for written resolution before start of fabrication. Final decision regarding the acceptance of proposed standards is the prerogative of the Purchaser.

- No deviation from the accepted standards shall be made subsequent to the Contract without the written approval of the Purchaser.

- Standards listed in individual equipment technical specification pertains mostly to the IEC, ISO, ANSI/IEEE, ASTM, NEMA as Purchaser’s references.

    - Designation of Trade Name or Catalogue Name and Number

- For convenience in designation in the Specification, certain equipment, articles, materials, or processes are designated by trade name or catalog name and number. Such designations shall be deemed to be followed by the words “or equivalent’ whether such words are shown or not, and the Supplier may offer any material or process which shall be equal in every respect to that so indicated or specified. The burden of proof of acceptability to the Purchaser, as to the comparative quality and suitability of alternative shall be upon the Supplier. If the Supplier’s request is not approved, the Supplier shall not ask or be permitted to use the same alternative materials or equipment in modified form.

    - Tropical Serviceability

      - General

- In choosing materials and their finishes, due regard is to be given to the humid tropical conditions under which equipment is to work. For both sheltered and unsheltered equipment, all materials and equipment supplied shall be suitable for delivery, storage and operation under tropical conditions of high temperature, high humidity, heavy rainfall, salty atmosphere and mildew and fungus-conducive environment and all conditions prevalent in the Purchaser’s country. When necessary, materials and equipment will be adequately treated and processed to meet these environmental conditions. The processes for tropicalization shall be in accordance with the best commercial and industrial practices. Some relaxation of the following provisions may be permitted only when equipment is hermetically sealed but it is preferred that tropical grade materials should be used wherever possible.

- Cubicles used for switchgear and control cabinets in outdoor plant shall be vermin-proof and fungus-proof.

- Totally enclosed motors and enclosures containing electrical control and switching equipment and instrument for outdoor installations shall be equipped with temperature controlled electrical heaters. The construction of the enclosures and installation of heaters shall be as to ensure effective circulation of air while ensuring that no damage to equipment occurs due to overheating.

- The Supplier shall supply the Purchaser with detailed descriptions of all design characteristics necessary to fulfill the requirements in connection with the tropical conditions under which the equipment will be operated.

      - Metals

- Iron and steel are in general to be galvanized or painted as appropriate.  Small iron and steel plate (other than SUS 316 stainless steel) of all instruments and electrical equipment, the cores of electromagnets and the metal parts or relays and mechanisms are to be treated in an approved manner to prevent rusting. Cores or other components which are laminated, or which cannot be rustproofed, shall have all the expected parts thoroughly cleaned and heavily enameled, lacquered or compounded. Where it is necessary to use dissimilar metals in contact, these should, if possible, be so selected that the potential difference between them in the electrochemical series is not greater than 0.5 volt. If this is not possible, the contact surfaces of one or both of the metals are to be electroplated or otherwise finished in such a manner that the potential difference from each other by an approved insulating material or a coating of approved insulating varnish.

      - Screws, Nuts, Springs, Pivots, etc

- The use of iron and steel is to be avoided in instruments and electrical relays wherever possible.  Steel screws, when used, are to be zinc, cadmium or chromium plated or, when plating is not possible owing to tolerance limitations, are to be of corrosion-resisting steel. All wood screws are to be of dull nickel plate brass or other approved finish. Instrument screws (except those forming part of a magnetic circuit are to be brass or bronze. Springs are to be of non-rusting materials, e.g., phosphor bronze or nickel silver, as far as possible. Pivots and other part for which non-ferrous material is unsuitable are to be of an approved rustproof steel where possible.

      - Fabric, Cork, Paper, etc

- Fabrics, cork, paper and similar materials, which are subsequently to be protected by impregnation, are to be adequately treated with an approved fungicide. Sleeving and fabrics treated with linseed oil or linseed oil varnishes are not to be used.

      - Wood

- The use of wood in equipment is to be avoided as far as possible. When used, woodwork shall be of thoroughly seasoned teak or approved wood which is resistant to fungal decay and shall be free from shakes and warps, sap and wane, knots, faults and other blemishes. All woodwork is to be suitably treated to protect it against the absorption of moisture, the growth of fungus and termite attack, unless it is naturally resistant to these causes of deterioration. All joints in woodwork are to be dovetailed or tongued and grooved as far as possible. Metal fittings where used are to be of non-ferrous material.

      - Adhesives

- Adhesives are to be specially selected to ensure the use of types which are impervious and resistant to attack of mildew and insects. Synthetic resin cement only shall be used for joining wood. Case-in cement shall not be used.

    - Performance under Site Environmental Conditions

      - General

- All equipment and materials to be furnished shall be capable of withstanding the operating environmental conditions specified, during storage and if susceptible to moisture absorption or fungus attack, shall be treated with fungicidal varnish and otherwise be adequately tropicalized as specified.

- Materials susceptible to deterioration from climatic conditions or subject to the formation of fungus or any other form of parasitic life shall preferably not be used, but if used and cannot be avoided, these must be permanently protected.

      - Seismic Requirements

- Equipment and equipment supports shall be designed to withstand and maintain their structural integrity when exposed to seismic loading.

    - Cleanliness

- At time of shipment, the equipment shall be clean inside and outside.

- All waste such as metal chips or filings, welding stubs, dirt, rags, debris and any other foreign material shall be removed from the interior of each component. All mill scale, rust, oil, grease, chalk, crayon or paint marks and other deleterious materials shall be removed from all interior or exterior surfaces.

- Cleaning of stainless steel surfaces shall be performed with solvents, cloths and abrasive that do not contain halide. Only stainless steel, clean, iron-free, hand or power tools and aluminum oxide abrasive shall be used on stainless steel components. Materials used to clean carbon steel or cast iron shall not be used to clean stainless steel surfaces.

    - Surface Treatment and Corrosion Protection

      - General

- Equipment and all steel parts (except for stainless steel surfaces) shall be painted or treated with protective coatings to prevent corrosion and provide a smart and pleasing appearance.

- Where possible, equipment shall be designed such that all surfaces can be finish-coated or recoated after erection at the site.

- All working of the materials (e.g. welding, drilling, grinding) shall be completed and surface defects (e.g. weld splatter, burrs, cracks, surface lamination and pitting) likely to be detrimental to the protective coating shall be eliminated prior to surface preparation.

- Welded joints shall be thoroughly steel-brush cleaned prior to the application of the first primer coat.

- The Supplier shall select a coating system to provide corrosion protection during shipment, storage and operation in the environment specified in this specification.

- All external cast iron, carbon steel and low alloy steel surface shall, as a minimum, be protected by application of a primer and top coat.

- Primer and top coat shall be by the same manufacturer.

- All external cast iron, carbon steel and low alloy steel surface shall be prepared for priming and by blast cleaning in accordance with the applicable Specification and the coating manufacturer’s recommendation. Surface preparation shall provide a substrate anchor profile height of 35 percent 5 percent of the primer dry film thickness.

- Primer shall be applied within eight (8) hours after blast cleaning and before rusting occurs.

- Stainless steel, galvanized, bronze and other non-ferrous surfaces do not require coating.

- Surfaces within 100 mm of field weld ends shall be protected with a certified-weld-thru primer or strippable protective coating.

- All machined cast iron, carbon steel and low alloy steel surfaces shall be coated with an easily removable (by alkaline solution, steam or hot water) corrosion preventative compound meeting MIL-C-16173, Grade 1 requirements. The Supplier shall inform Purchaser of the name, make, type, properties and removal instructions of the compound he intends to use.

- The Supplier shall furnish, with his proposal, a complete description of the corrosion protection he intends to provide. After purchase order, the Supplier shall submit applicable cleaning and coating procedures and specific description of coating material to be used.

- The colour of successive coats of paint must be sufficiently different to allow easy identification of the sequence of painting on surfaces for control purposes.

- The paint film must adhere perfectly to the painted surface.

      - Control cabinets, panels and cubicles

- Treatment of control cabinets, panels and cubicles shall be as follows:

- Thorough surface treatment

- Two base coats of 2-component zinc-chromate epoxy resin primer (min. total dry film thickness: 80 microns)

- Two top coats of 2-component epoxy resin enamel (min. total dry film thickness: 100 microns)

- The Purchaser reserves the right to determine the thickness of coating by making appropriate tests.

- For such tests, the Supplier shall make available the apparatus to be used.

- The paint film, under visual examination, must in any case present the appearance of an accurate application and be free of lesions, porosity, cracks or bubbles.

      - Guarantees

- The guarantee period of the paint work shall be two (2) years. During this period, it will be the responsibility of the Supplier to repair or replace without charge all paintwork showing defects (such as discoloration, peeling, wrinkles, bubbles, flakes or rust, etc.) where it may be proven that the deterioration arises from:

- Poor quality paint;

- Insufficient cleaning of the surface before painting;

- Incorrect choice of paint for the service required; and

- Incorrect application of paint itself to the surface.

- In such cases, the Supplier shall take charge of restoration of all parts which have shown defects.

- The guarantee shall commence on the day of the issuance of the Certificate of Provisional Acceptance.

    - Painting

- Due to the unfavourable atmospheric conditions, particular attention shall be given to the corrosion protection of all metal parts of equipment not installed in air-conditioned rooms.

- All surfaces shall be thoroughly cleaned of rust, scale, grease and dirt and other foreign matter and all imperfections shall be removed by means of approved methods.

- The following treatments shall be applied:

a)	 External surfaces:

- All steel surfaces  shall be sand-blasted  in accordance with DIN 55928 Part 4 (equivalent to SIS 055900), and shall then be painted in the following sequence:

1.	one (1)	primer coat				60µm

two-component epoxy zinc-phosphate

2.	one (1) 	intermediate coat			60µm

two-component epoxy micaceous iron oxide

3.	one (1)	top coat				40µm

two-component polyurethane

- Total coating thickness (dry-film incl. tolerances) min. 160µm

- The final coat of painting shall be of pore-free and homogeneous quality and shall be of an uniform non-glossy shade of colour code RAL 7032 (silica-grey). For extensions the colour code of the existing units shall be applied.

- If any hot-dip galvanised steel parts will be provided the same painting method shall be applied. However, instead of the primer coats or zinc powder coat one adhesive coat and one base coat shall be applied. In this case, the minimum thickness of galvanising shall be 55 µm.

- In case of ordinary stainless steel the primer coats may be replaced by a suitable undercoat.

- Mechanical damage of painting shall be repaired at site with the same type of painting as above.

b)	  Internal surfaces:

- Inside the transformer and reactor vessel, sand-blasting shall be performed in accordance with DIN 55928 Part 4 (equivalent to SIS 055900). After that, an oil-resistant insulating coating shall be applied to all steel surfaces in contact with the oil (e.g. tank, cover, core steel plates etc.).

- The minimum dry film thickness shall be 35 µm (Colour code RAL 9010 (white) or equivalent).

    - Preparation for Shipment and Storage

- The Supplier shall prepare equipment for shipment to protect it from damage during shipment and subsequent storage not exceeding one year, unless specified otherwise in the Technical Data Sheets for each equipment under this specification.

- Equipment shall be completely drained of all water and thoroughly dry prior to shipment. When such draining requires removal of plugs, drain valves, etc., the Supplier shall make sure that these parts are reinserted or reassembled prior to shipment.

- All openings and  machined surfaces shall be provided with protection to prevent damage, corrosion and entrance of foreign matter during shipment and storage.

- Flanged connections shall be protected by a 12.5 mm or thicker plywood disc, or suitable alternate, bolted to the face of the flange.

- Treaded or socket weld connections shall be protected with screwed or snap-in (snap-on) type, securely held, plastic protectors. Cast-iron plugs are not acceptable for protection unless part of the permanent assembly.

- Butt weld connections shall be protected by wooden disks that cover the entire weld end area, and are secured by metal straps and fasteners.

- Covers, straps or fasteners shall not be welded to equipment.

- Equipment shall be adequately supported for shipment. All loose parts shall be crated or boxed for shipment and appropriately identified. If equipment is braced internally for shipment it shall be marked conspicuously, “Remove internal braces before testing and operating”.

- The outside of all containers, cases, etc. shall be clearly marked with the total weight, point of maximum weight and correct position for the attachment of lifting hooks and cables and shall bear identification marks relating to the appropriate dispatch documents. Where appropriate, the cases or boxes shall bear special instructions such as “top”, “handle with care”, “keep dry”, etc.

- All large and heavy shipping units shall have suitable skids for moving. Crating shall also be adequate for lifting with slings. If location of slings is critical, these locations shall be marked accordingly.

- The storage will be in an environment similar to the installed location, i.e., indoor equipment will be stored indoors (without heating and ventilation), and outdoor equipment will be stored outdoors. Where required to protect against condensation and humidity, a desiccant shall be provided and its presence, with the need of periodic removal and dryout, shall be so marked.  When electric space heaters are provided for that purpose, these should be wired to the outside of the equipment so that energizing immediately upon receipt is possible without disassembly of crates, etc.  This also requires that no combustible materials be left in the inside of the equipment.

- Items which maybe subjected to open storage for several months on site shall be suitably packed and protected from the weather.

- The Supplier shall provide storage and handling instructions including descriptions for periodic inspection and/or storage maintenance to ascertain that no deterioration will occur during storage. One set of these instructions shall be fastened securely to the outside of the shipping unit.

- The Supplier shall provide at Purchaser’s request, the Supplier recommended instructions for long term storage.

- When an equipment is specified for export shipment, the Supplier shall include packaging adequate for export shipment, and this packaging shall be such as to obtain approval and acceptance by transportation companies.

- All equipment shall be shipped from the factory completely assembled as far as practicable, subject to the limitations of length, height, depth, and weight, etc. described in the Special Conditions of Contract or in the Technical Data Sheets for each of the equipment under this Specification.

    - Equipment Designation (Equipment Marking)

      - Identification System

- All equipment and all component parts including cables, control wiring and terminals shall be designated with an alphanumeric code allowing clear identification of the equipment and components during design, installation and operation of the plant/substation. Equipment, cables, control wiring and terminals shall be systematically marked, both on the drawings and documents and on the equipment, cables, wires and terminals themselves.

- Equipment designation codes (E.D.S.) shall be indicated on all planning documents including bills of materials, lists of spare parts, etc. The codes will later be used for easy identification of stored equipment parts and materials and shall be suitable for use with a computer supported registration system.

- Bid drawings are in some cases already marked with designated codes; the system shall be expanded to include detailed diagrams, cable lists, spare parts list, etc. approved by the Purchaser.

- Wherever applicable, labels/plates bearing the E.D.S. code shall be attached to equipment in the Supplier’s works.

- The material and fastening methods proposed for E.D.S. labels/plates are subject to the approval of the Purchaser.

      - Labels and Plates

- A corrosion-resistant nameplate with clearly legible writing shall be permanently attached to each assembled piece of equipment at an easily visible place. It shall provide all necessary information pertaining to the equipment, but as a minimum, the following must be included:  Manufacturer’s name, type of equipment, serial number, year of manufacture, project identification number, weight, E.D.S. code and other relevant information in compliance with applicable standards. Any special maintenance instructions shall also be shown at this or other suitable location.

- If it is not practical to include Purchaser’s equipment identification, or tag number on the equipment nameplate, then a separate durable stainless steel tag with Purchaser’s identification number shall be provided and securely attached to the equipment.

- Labels shall also be provided for equipment and devices mounted on control boards, relay cabinets, desks and other places as required for proper identification, as well as for operational, functional and safety reasons. The labeling, size of label-plates and their location shall be subject to approval by the Purchaser. A sample label-plate (with indication of material used) with lettering shall be submitted for this purpose.

- Wherever necessary, cautionary and warning plates and signs shall be provided. Nameplates, labels and warning plates shall be in English.

- The manufacturer must paste the QR code on the main equipment (Circuit Breakers, Disconnectors, Current Transformers, Voltage Transformers, Surge Arresters) he manufactures for this package. The QR code is implemented in accordance with regulations 1188/QD-EVN dated September 01, 2022, 6522/EVNNPT-VTCNTT dated December 01, 2024 and will be provided to the Bidder by the Investor after 30 days from the approval of the equipment manufacturing drawings (final drawings). The device must be pasted with a QR code from the factory.

    - Interchange ability and Standardization of Small Equipment

- All like parts shall be fully interchangeable with no requirement for alteration or adjustment.

- The Supplier shall be responsible for the standardization of all small equipment, materials and devices he would supply. He shall arrange and perform the necessary coordination work with his manufacturers for the purposes of such standardization.

- All equipment, parts and elements of mass production shall be standardized. Such items of equipment, parts and elements shall include, but shall not be limited to, the following;

- Power Supply units

- Printed Circuit Boards, microchips

- Electrical instruments and measuring devices

- Terminals and terminal boxes

- Primary, secondary and auxiliary relays

- Contactors, fuses and switches

- Lamps, LEDs, bulbs, sockets, plugs, push button, etc.

- etc.

- In order to achieve standardization with equipment or elements to be supplied under other contracts, the Purchaser reserves the right to impose upon the Supplier the type and brand of preferred equipment or element.

    - Spare Parts

- The Supplier shall include with his Bid, a list of spare parts which he considers necessary for safe and reliable operation and maintenance for the initial period of three years. The Supplier shall indicate the expected life of the parts requiring replacements and the minimum recommended inventory of the spare parts for installation, start-up, continuous operation and maintenance. Supplier shall state whether the recommended spare parts is a stock item or a special item, and shall furnish name and location of the nearest Supplier, and approximate lead time required for delivery.

- All spare parts shall be readily interchangeable with the ones which they are to replace. They shall be of the same material, of identical size and manufacture and shall have the same properties as the corresponding parts of the installed equipment. Specified conditions relating to tests, treatment of surfaces and painting, etc. of the installed equipment shall also apply to spare parts.

- All spare parts shall be properly packed (and where necessary treated) in such a manner as to allow prolonged storage at the Site, considering the ambient conditions prevailing there. In due time, the Supplier shall inform the Purchaser of the eventual precautions to be taken for the proper storage of the spare parts.

- The Supplier shall provide a spare parts list containing at least the following information:

- Name and address of manufacturer and other identification no.

- Item description including EDS-code, drawing no., material designation, units to be ordered.

- List of items (designated by EDS-code) for which the respective spare parts can be used.

- Item price.

    - Quality Assurance Requirements

      - General

- The Supplier shall have a well-organized Quality Assurance Program (QAP) based on ISO 9001 (Quality System Model for Quality Assurance in design/development, production, installation and servicing) to assure that items and services, including subcontracted items and services, comply with this specification.

- All design, manufacturing, processing, testing and inspection operations affecting the equipment or material shall be governed by Quality Assurance procedures in accordance with the directives of the ISO 9001 standards while the production and installation shall be governed by quality assurance procedure in accordance with the directives of the ISO 9002 standards. These may be subject to surveillance by Purchaser or Purchaser’s representative. A tentative QAP shall be submitted together with the bid and shall meet the requirements.

- Prior to production, the Supplier shall submit to Purchaser a fabrication sequence describing inspection and/or tests to be performed, for use in determining inspection points which Purchaser may desire to witness. Purchaser will advise the Supplier prior to production of those fabrication steps and shop inspection points that Purchaser desires to witness.

- The Supplier shall give Purchaser adequate notice, forty five (45) calendar days minimum, prior to those fabrication steps and tests which Purchaser desires to witness.

      - Quality Assurance Program

- The Supplier shall, for all work covered by the Contract, establish and implement a quality assurance program which as a minimum, meet the requirements set out in ISO 9001 and ISO 9002.

- In addition to the requirements of these ISO’s, the Supplier shall:

- Establish procedures for adequate planning and resourcing of all quality related activities including the preparation of quality plans.

- Establish measures for the identification and control of items throughout all stages of the Contract. This shall include measures to maintain traceability as identified in agreed quality plans.

- Arrange for the protection of the quality of the product to include delivery to the specified destination.

- Control their measuring and test equipment in accordance with established procedures for measurements and calibration systems and ensure that such equipment that may be used by subcontractors to verify work is similarly controlled.

- Ensure adequate quality systems exist for compliance with the requirements.

- Where any site installation and/or test and commissioning work is involved, the Supplier shall prepare contract-specific quality assurance procedures in agreement with the Purchaser prior to commencements of such works.

- The Supplier shall be responsible for specifying the quality assurance requirements to his subcontractors, for approving subcontractors quality assurance program and for ensuring compliance with the requirements.

- The Supplier shall ensure that all appropriate technical information is extracted from the Contract documents and specifications and passed on to the subcontractors.

- The Supplier shall ensure that all computer systems and software to be utilized on the project is qualified for the application under consideration and such qualification is documented.

      - Quality Plans, Inspection and Test Schedules

- Quality plans shall be prepared detailing the specific activities, design reviews, operations, control procedures, inspections, testing, approvals and certification requirements applicable.  Quality plans shall be submitted to the Purchaser for review and approval.

- Where inspection schedules are generated in support of a quality plan, these are also required by the Purchaser for review and approval.

- The format and content of schedules shall ensure that inspection operations are planned and performed in a systematic manner.

- Documents referred to in quality plans shall be available to the Purchaser for review if required.

- Specific quality plans shall be prepared for site work and submitted for review and approval by the Purchaser prior to commencement of such work.

- The Supplier shall approve all quality plans, inspection and test schedules of their subcontractors and vendors.

- The Supplier shall identify his verification requirements on the quality plans submitted to the Purchaser for review and approval and shall identify the following:

- Stages subject to random surveillance.

- Inspection that require to be carried out or witnessed, by the Purchaser or a third party following satisfactory verification and acceptance by the Supplier.

- Hold points beyond which work cannot proceed before completion of all operations, verifications and related activities identified after the previous hold point on the quality plan.

- The Supplier shall be responsible for identifying and arranging any verification activities for statutory approval in the country of manufacture.

- The Supplier shall adhere to the reviewed quality plan(s) and notify the Purchaser immediately of any deficiencies or difficulties that would arise.

- Where functional testing is required, functional test schedule(s) and/or procedures shall be prepared by the Supplier and submitted to the Purchaser for review and approval prior to the commencement of such testing.

      - Monitoring by the Purchaser

- During the course of the Contract, Purchaser reserves the right to monitor the implementation of the Supplier’s quality assurance program. Monitoring will be by means of surveillance of activities at the work locations and where appropriate by formal audits. Representatives of the Purchaser shall be afforded unrestricted access and facilities at all reasonable times to carry out this work to verify manufacturer’s compliance with the established manufacturing, assembly, delivery, including installation and commissioning schedules.

- Purchaser reserves the right to monitor subcontractor’s activities and the Supplier shall ensure that subcontractors are informed of these requirements.

      - Records

- The Supplier shall generate records as required by the quality assurance system and quality plans. Records, including audit reports shall be made available for inspection by Purchaser.

- All records shall be concisely compiled, indexed and cross referenced to the project contract number and they were relevant subcontract numbers. They shall be clearly identifiable to the individual parts and assemblies to which they refer.

- Those records required by the Purchaser, as defined in the contract specifications and quality plans shall be available at the time of delivery of the equipment. Such records shall include reports and certification in respect of pressure retaining components together with general traceability records for all items through certification and build documentation as a minimum.  Four (4) copies of these records shall be supplied to Purchaser with the exception of radiographic films where the original set of films shall be supplied.

- All records generated during the course of the Contract, including those generated as evidence of effective implementation of the quality assurance program of the Supplier and his subcontractors, shall be retained by the Supplier for a minimum period of five (5) years from the date of contract completion.  These records shall be made available to Purchaser on request during the retention period.

      - Sub-orders

- All orders for materials and equipment purchased by the Supplier specifically for this Contract are subject to inspection, tests and expediting.  The manufacturer shall be advised by the Supplier for these interventions by the Purchaser or his authorized representative(s).

- The QA program shall contain a detailed list of all sub-orders placed with sufficient information to enable the inspectorate to function properly, including order numbers, manufacturer’s identity, equipment specifications, delivery and dispatch dates, etc.

      - Material and Test Certification

- One (1) copy of all tests results recorded during an inspection visit shall be handed to the Purchaser or his authorized representative(s) on that day.  In addition, six (6) copies of the test certificates will be required fifteen (15) days thereafter.

- In the event that the inspection of any item is waived, test certificates shall still be required.

      - Particular QA Requirements

        - General

- As a supplemental document to the QA program, the Supplier shall submit for approval of the Purchaser a separate document with detailed particular requirements and specific acceptance criteria of all equipment.

        - At Shop

- Corresponding to each major and minor equipment, the following data are required for submission to and approval of the Purchaser:

- Test and inspection procedure;

- Guaranteed technical rated or design data;

- List of holdpoints and/or routine tests;

- Acceptance criteria and reference standards;

- Form of test results/data with comparison to the guaranteed data. All allowable tolerances with respect to dimensional control of assemblies and sub-assemblies at shop shall be clearly indicated in the manufacturer’s drawings.

      - Packing and Marking

- Careful packaging of all materials supplied for this Contract is of utmost importance and is subject to the control of the Purchaser, so that the following aspects are checked:

- Packaged design and markings;

- Protection of contents against damage by mechanical shock, moisture ingress and adverse atmospheric conditions, corrosion;

- Material quality workmanship and manufacturing of packages.

      - Reporting and Corrective Action

- The Supplier’s Quality Assurance Program shall provide for prompt detection and correction of all conditions adversely affecting quality, including failures, malfunctions, incidents, trends, deficiencies, deviations, non-conformances and defective materials. The Supplier shall establish and maintain methods for verifying and determining the cause of an adverse condition and for initiating necessary improvement and corrections to preclude repetition.  Quality trends shall be analyzed to furnish a basis for improvement in work performance. The Supplier’s corrective action system shall extend to the performance of other participating contractors, sub-contractors, and Suppliers, when necessary, and shall provide for the interchange of corrective action information. Identification of the adverse condition, its cause, and the corrective action taken shall be recorded and reported to appropriate levels of management.

- The Supplier shall establish and implement procedures for reporting, verifying, analyzing and correcting failures, including those that occur during development and qualification testing. The procedure shall provide assurance that the cause and mode of each failure are determined, that potential safety and availability implications are evaluated, and that corrective action is taken.

- A failure report shall be prepared to identify the failed item and its origin or source of manufacture and shall describe the failure, the test status at time of failure, the probable cause and mode of failure, and the recommended corrective action.

      - Design Revision and Substitution of Material

- Any revision affecting the design and manufacturing of the equipment as well as substitution of materials that is deemed necessary shall be notified by the Supplier to the Purchaser for the latter’s review and approval.

    - DESCRIPTION OF EQUIPMENT AND MATERIALSFOR SUBSTATION

- All materials and equipment to be supplied, shall be new and unused, and shall incorporate all recent improvements in design and materials unless provided for otherwise in the contract.

- Wherever in these specifications reference is made to standards or codes to be met by the goods and materials to be furnished or tested, the provisions of the latest current edition or revision of the relevant standards shall apply, unless otherwise expressly stated in the Contract. Where such standards and codes are national or relate to a particular country or region, other authoritative standards that ensure substantial equivalence to the standards and codes specified will be acceptable.

      - CIRCUIT BREAKERS

    - 220kV Circuit breaker, 110kV Circuit breaker

#### General

- Comply with the Technical standards of 110kV, 220kV and 500kV outdoor circuit breakers in National Electricity of Vietnam issued together with the Decision No. 272/QĐ-EVN dated April 24, 2019 and 190/QĐ-HDTV dated 04/12/2024 of Electricity of Vietnam, Decision No. 1677/QĐ-EVNNPT dated August 20, 2025 and No.2416/QĐ-EVNNPT dated 09/12/2025  of the National Power Transmission Corporation promulgating regulations on basic technical characteristics of 500kV, 220kV, 110kV circuit breakers on the transmission grid.

- Definition of power transmission grid circuit breaker:

- Circuit breakers have the ability to close/open in normal operation mode and tripping in abnormal or fault operating modes of the power grid with rated voltage level. The circuit breaker must meet the durability for climatic and environmental conditions in Vietnam: tropicalized, suitable for installation and operating environment conditions.

- The basic standards for applying the design, manufacture and testing of circuit breakers in the power transmission grid are IEC 62271-100 and IEC 62271-1.

- General requirements on standards and environment:

- The circuit breaker on the power transmission grid which is manufactured and installed must meet Vietnamese regulations and standards, electrical standards, IEC/IEEE standards and be able to work stably in working conditions, including climate and natural environment of Vietnam.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition			: Tropical

- Maximum air temperature		: 45°C

- Minimum air temperature		: 0°C

- Average air temperature		: 25°C

- Maximum humidity		: 100%

- Average humidity			: 85%

- Creepage distance			: 31mm/kV

- Seismic factor 			: 0.15g

- Depending on the natural conditions of the installation location of the equipment, as defined in QCVN 02:2022/BXD , the above values of environmental conditions may change to suit the actual requirements to be applied.

Requirements of the electrical system installing the circuit breaker:

| Item | 220 kV system | 110 kV system |
| --- | --- | --- |
| Normal Voltage | 220 kV | 110 kV |
| Rated Frequency | 50 Hz | 50 Hz |
| Max operating voltage | 242 kV | 121 kV |
| Min operating voltage | 198 kV | 99 kV |
| Connection diagram | 3-phase 3-wire | 3-phase 3-wire |
| Neutral grounding mode | Direct | Direct |
| Ground fault factor of transmission grid | <1,4 | <1,4 |

- Requirements for quality certificates:

- The manufacturer must have a certificate of the quality management system (ISO 9001 or equivalent, still valid) applied to the production of the Circuit breaker. The manufacturer must have a factory testing laboratory with certified testing equipment.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, trade and technical labels, etc.

#### Requirement component parts of for circuit breaker

- Circuit breaker

- The circuit breaker is designed and manufactured in accordance with IEC 62271-100 standard so that it can be installed outdoors in the operating conditions of Vietnam's power transmission system. The circuit breakers in the power transmission grid are usually applied single-phase type, each phase has a operation mechanism. For level voltage from 110 kV or less, 3-phase type, 3-phase operation mechanism can be applied. In addition to IEC 62271-100 standard, circuit breakers must meet IEC 62271-1, IEC 62271-101, IEC 60060 standards and must meet requirements for insulation strength, temperature rise during long-term operation.

- Circuit breakers are designed and manufactured to ensure safe operation under normal as well as fault conditions, to withstand atmospheric overvoltages, overvoltage phenomenon occurs when switching operation or tripping fault circuit. The technical requirements for circuit breaker voltage shall be specified in Datasheet.

- Operating duty cycle of  circuit breakers is: O - 0.3sec - CO - 3 min. - CO and close or open time for three pole discrepancy is less than or equal to 4 milliseconds.

- Circuit breakers shall be properly designed and constructed so that easily inspected and quickly replaced if it has any defective/damaged of contact chambers or other components. The components parts of circuit breakers after assembly do not form holes for birds to nest that can cause of problems.

- Interrupting chamber

- Circuit breakers with voltage level of 220 kV or less have usualy only one of arc extinguishing chamber. Circuit breakers with isolated and arc extinguish by sulphur hexafluoride (SF6) gas insulated. The arc-extinguishing chamber must meet the requirements of SF6 gas system tightness with gas leakage ≤ 0.5%/year of the entire gas volume.

- SF6 gas or insulating and arc-extinguishing materials shall meet the detailed requirements in IEC 60376 standard. All materials used in the construction of SF6 circuit breaker shall be suitable for the working conditions in the atmosphere of SF6 gas and the decomposition products of SF6. The circuit breaker shall be able to withstand the maximum pressure during operation without gas leakage or deformation damage.

- The subsidiary company of EVNNPT must be equipped with gas filling devices suitable for each type of SF6 circuit breaker currently operating, performing maintenance, and installing on the power transmission grid.

- The gas system of the interrupting chamber must have a gas pressure meter with temperature compensation function, and a monitoring device to detect SF6 gas leakage at two levels: Alarm warning mode for SF6 gas density threshold at level 1, alarm warning and lock control for SF6 gas density threshold at level 2 (lockout). The mass and density of SF 6 gas , the warning levels of level 1 and level 2 mentioned above must be clearly stated on the circuit breaker nameplate.

- Each phase of the circuit breaker is equipped with one-way valve, which is convenient for filling and discharging SF6 gas.

- The contacts of circuit breaker are made of a non-abrasive material, resistant to compression contact, resistant to the high temperatures generated by arcing in the interrupting chamber and ensuring long-term operation throughout the life of the circuit breaker.

- The operating mechanism is made of non-corrosive, high-strength metal materials without rust. The operating mechanism must be equipped with an anti-skid lock which operates the mechanism. Have a closed structure so insects do not get in. The main drive rod in the CB pole is made of insulating material, has high mechanical strength, moisture resistance, resistance to SF6 gas and SF6 decomposition products.

- Insulation and poles post of circuit breaker

- Pole post and supporting porcelain post of circuit breaker must be made of non-assembled cylindrical porcelain, canopy circle, brown color according to IEC 62155 or equivalent. Porcelain must have thermal, mechanical and electrical durability, operate in accordance with the environmental conditions and technical characteristics listed in datasheet.

- In the compartments of the pole column, there must be equipped dehumidifying apparatus, decomposition product filter of SF6 gas and pressure release device to ensure the interrupting chamber does not explode when the pressure increases suddenly. Connection between poles or other parts by bolts.

- Insulation and poles post of circuit breaker are manufactured to ensure that the distances from live parts to earth and between live parts comply with the requirements detailed in datasheet.

- Requirements for control cubicle, Operating mechanism cabinet

- Operating mechanism cabinet:

- Each circuit breaker shall be equipped local control cabinet with operating mechanism, control switches and corresponding relays, switches, terminal clamp for control cables, Counter of the number of closing-opening operations of the circuit breaker, LED lighting,  heating reactors with thermal relays and other auxiliary equipment.

- The secondary terminal clamps must be extended at locations with multiple connections to prevent connecting multiple conductors in the same location. The number of terminal clamps  for spare at least 20% of the connected terminal. Terminal for closing circuit or tripping circuit not located close to AC or DC power terminal.

- Operating mechanism cabinet of the circuit breaker is equipped with the following parts:

- Switch selection of LOCAL/REMOTE position (or can be installed in the control cabinet according to the manufacturer's technology).

- Switch selection of ON/OFF position in local (or can be installed in the control cabinet according to the manufacturer's technology).

- Counter of the number of closing - opening operations of the circuit breaker.

- Auxiliary contact system and limit switch to control the spring motor and alarm signal the status of spring storage.

- There is a spring charge status indicator: in the form of symbols/or letters to identify spring status of the circuit breaker is charged and not charged.

- The indicator of the open /close status of the circuit breaker.

- The number of auxiliary contacts in each phase of the circuit breaker must comply with the requirements in datasheet.

- The Operating mechanism shall be capable of locking at the closed or open position of the circuit breaker and shall be capable of opening or closing after recloser period.

- The Operating mechanism and associated equipment must be able to withstand the operating forces of the circuit breaker in accordance with IEC 62271-100 and have a safe mechanical operation duration of at least 10000 times.

- Having open-close status and spring charge status indicator of circuit breaker for easy identification without opening the door of the cabinet.

- The capacity of closing coil and tripping coils must not exceed 1200VA for all 3 phases. The required capacity may be greater in case of close/open time is faster than the value specified in datasheet.

- The Operating mechanism cabinet can be made of aluminum alloy or stainless steel (Inox 304) and can be painted on the surface of the cabinet in accordance with the general specifications. The Operating mechanism cabinet has a minimum thickness of 2 mm. The control cabinet must withstand extreme weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets.

- Common control cubicle:

- For voltage level from 220 kV and lower, the control cabinet can be integrated with the Operating mechanism cabinet of 1-phase or 3-phase circuit breakers.

- The common control cabinet is made of aluminum alloy or stainless steel (Inox 304), the cabinet has a minimum thickness of 2 mm. The control cabinet must withstand severe weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets. Cabinet door designed with latch lock and key lock, gaskets have long service life in outdoor environment conditions. It is recommended to install the control cabinet at the position nearest to phase B. The control and protection circuits linking the control cabinets with the operation mechansim cabinets in the phases are recommended to use specialized cables and jacks manufactured by the manufacturer and supplied synchronously with the circuit breaker.

- Circuit breaker control circuit using 220VDC power supply, including:

- 2 trip circuit working at 220VDC voltage with permissible voltage deviation (+10%; -30%) provided by 2 independent sources;

- 1 closed circuit working at 220VDC voltage with permissible voltage deviation (+10%; -25 %).

- The heating and lighting circuits in the cabinet use 220VAC power with voltage deviation (+10%; - 15 %).

- Equip the following equipment at the local control cabinet of the circuit breaker:

- Switch selection of Local/Remote position (in which: Local: selects local operation; Remote: selects remote operation).

- Control switch On/Off operation in local: can use the self-return switch type or the “OPEN/CLOSE” push buttons.

- The secondary terminal clamps must be able to expand at locations with multiple connections to prevent connecting multiple conductors in the same location. The number of terminal clamps for spare at least 20% of the connected terminal. Terminal for closing circuit or tripping circuit not located close to AC or DC power terminal. The power supply cable is independent of the control cable.

- The control cabinet must be equipped with auxiliary relays, time relays, magnetic starters, and overcurrent and overvoltage protection circuits for motors, which should be placed in the common control cabinet to avoid damage caused by vibrations arising from operation mechanism when switching circuit breakers.

- Inside cabinet have common grounding copper rod with pre-drilled holes and attached nut bolts for grounding connection.

- The control cabinet must be equipped with the following systems: automatic heating, automatic lighting by led lights, AC sockets, MCB with auxiliary contacts.

- Operational requirements:

- Spring mechanism can be charged by manual and electric. In normal operation, the electric spring recharge shall begin immediately and automatically when the end of a closing cycle, the spring recharging time shall not exceed 15 second. The process of storing the spring is not interrupted until the spring is fully charged. When the closing spring is not fully charged, the lock cannot close the circuit breaker.

- Spring charge motor uses a DC voltage of 220 VDC and is recommended to use an additional 220 VAC source (depending on actual conditions at the substation). The spring charge motor must operate normally with the supply voltage deviates within (+10%; -15%) from the rated value of the DC or AC power supply. There is an overcurrent and overload protection circuit for the motor.

- The circuit breaker must have a device to prevent simultaneous remote control with local control. There is protective circuit for anti-pumping, operation locking circuits (lockout), signals (alarm); signal circuit of error spring stored and locks the circuit of the spring motor, non-synchronous phases protection circuit, electrical interlock circuit when one of the following cases occurs: SF6 gas pressure drops below rated value, spring is not fully charged, tripping circuit damage.

- Cable requirements:

- AC and DC power cables are provided with separate cables, cross-section not less than 2.5 mm2. Control and signal cables use cables suitable for the manufacturer's circuit breakers, with a cross section of not less than 1.5 mm2. Secondary cables used are waterproof, fireproof, the shielded to interference-proof and copper cores with high quality, many fibers. For the single-phase circuit breakers, the connection between operating mechanism cabinets and common control cabinet should be use cable with Plug-in prefabricated jacks which supplied synchronously with circuit breakers manufacturer.

- Installation arrangement

- Circuit breakers shall be suitably designed for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm. The steel for the support is highly durable, withstands the loads of the circuit breaker and meets the requirements of the circuit breaker manufacturer. The cross-section of the support structures must be large enough to reduce vibration when operating the circuit breaker. Steel parts (support structures, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 with coating thickness not less than 80 µm , the current standards for dip galvanizing, bolts and nuts.

- In case the operating mechanism cabinet (control cabinet) of the circuit breaker is designed and installed with a height of more than 1.3 m above the ground, it must be attached with operator’s stand.

- Non-electric metal structures parts, equipment enclosures, operation mechanism cabinet enclosures, control cabinets enclosures etc. of the circuit breaker must be directly earthed into the common grounding system of substation at the installation site. The grounding point of the circuit breaker must have the symbol "grounding", located at a convenient location to connect the grounding system of the substation. The cabinet enclosures and the cabinet door of the operation cabinet and control cabinet are grounded with multi-strand copper wire with insulated sheath, the cross-section of the copper wire is not less than 1.5 mm2.

- Circuit breaker must be attached to the Parameter Table and the circuit breaker label is made of aluminum alloy or stainless steel (Inox 304) , fully showing the main parameters of the circuit breaker according to IEC 62271-100. The data in the Parameter Table and the circuit breaker label must be highly durable, not lose color and always read clearly during the operation of the circuit breaker.

- During the installation process, must strictly follow the installation process, install the circuit breaker according to the instructions of the manufacturer; use materials and accessories for CB to ensure quality, in accordance with the requirements of the manufacturer. The entire process of installing and setting the circuit breaker must be carried out under the supervision of a specialist from the manufacturer or a supervisor must have a certificate issued or authorized by the manufacturer. In the record of acceptance of the installation of the circuit breaker or the test of setting a new circuit breaker must be signed by the qualified supervisor mentioned above.

- Accessories of circuit breaker

The circuit breaker must be equipped with the following accessories:

- The Terminal suitable for connecting conductors/bars and circuit breaker terminals are made of aluminum alloy.

- Stainless steel bolts, nuts, washers respectively.

- The structure and support of the CB.

- Contact grease, lubricating grease, specialized paper for cleaning the contact surface, spare rubber gaskets, SF 6 gas are enough for the first gas charge for the circuit breaker at the site.

- Specialized tools specific to CB: installation tools, manual tools for the CB and for the operating mechanism storage unit.

- Other requirements for circuit breaker

- Circuit breaker is new 100%, no defects; certified origin (CO) is clear, legal; CB has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- The manufacturer undertakes to warrant the equipment according to current commercial regulations as well as regulations on ensuring the technical life of the equipment stated in “Item (3) Equipment life requirements” of this Regulation.

#### Equipment life requirements

The reliability requirements as well as the life requirements of the circuit breakers are determined with the following minimum conditions:

- The number of safe mechanical switching operations is not less than 10000 times (equivalent to class M2).

- Number of times of switching operations at rated current is not less than 2500 times.

- The number of times O-t-CO-ta-CO rated cycle operation is not less than 500 times.

- Number tripping for breaking times corresponding to the value of 50% of the rated short-circuit breaking current is not less than 30 times.

- Number tripping for breaking times corresponding to the value of 100% of the rated short-circuit breaking current is not less than 10 times.

#### Requirements for testing for circuit breaker

1. General requirements for test documentation:

Supplied circuit breakers shall be accompanied by adequate documentation demonstrating ability to meet the above technical specifications as well as IEC standards specified for each component of the equipment.

Manufacturer and /or supplier of circuit breaker is responsible for providing a full records, Type test, factory test (Routine test) demonstrating the ability to meet working requirements for supplied equipment, in which:

a. The type test report shall be issued by the independent testing laboratories which are member of STL organization (Shorting Testing Liasion).

b. The Routine Test reports are made and issued by the circuit breaker manufacturer.

2. Test requirements for circuit breakers:

The design, manufacture and testing of circuit breakers shall comply with IEC 62271-100 or higher. The manufacturer shall provide the following test documents:

a. Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

It is required to provide documents of seven type tests according to IEC 62271-100 standards as following:

- Dielectric test.

- Temperature rise tests.

- Measurement of the resistance of the main circuit.

- Short-time withstand current and peak withstand current tests.

- Short-circuits current making and breaking tests

- Additional tests on auxiliary and control circuits.

- Mechanical operation tests at ambient temperature (class M1).

For the following cases:

-	The 500 kV, 220 kV, 110 kV circuit breakers have special requirements on switching overvoltage and rate of rise of the transient recovery voltage.

-	Special cases shall be decided by competent persons.

The manufacturer may be required to provide documents proving partial or total compliance with the following 11 types of tests according to IEC 62271-100:

- Test to verify the degrees of protection of enclosures;

- Tightness tests;

- Humidity test;

- Extended mechanical endurance tests on circuit breakers for special service conditions, class M2 rating;

- Low and high temperature tests;

- Critical current tests;

- Short-line fault tests;

- Out-of-phase making and breaking tests;

- Single-phase fault test;

- Switching of shunt reactors and motors as specified IEC 612271-110;

- Capacitive current switching tests;

- Line-charging current breaking test

- Cable-charging current breaking test

- Single capacitor bank switching test

- Back-to-back capacitor bank switching test

b. Routine test:

The manufacturer must provide documents of six routine tests according to IEC 62271-100 standards as following:

- Dielectric-test on the main circuit.

- Tests on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Tightness test.

- Design and visual checks.

- Mechanical operating tests.

The manufacturer is responsible for providing a records, routine test results of the above tests.

#### Requirements for transporting of circuit breaker

- Circuit breaker’s components is possible to remove or packing with a table listing the number of equipment and material supplies in each package for easily stored, transported by machine or manually, allowing re-installation and operation easily.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration, the impact of sea water, thunderstorms as well as other environmental influences.

#### Requirements for documents of circuit breaker

It is the responsibility of the manufacturer to provide complete documentation of the following:

- Table of required parameters for circuit breakers.

- Drawings describing the structure, dimensions and cross-sections of the main components of the equipment: circuit breakers, poles, operation mechanism cabinets, control cabinets; quantity, drawing, specification of circuit breaker gaskets and circuit breaker accessories.

- Principle drawing and internal connection of control cabinet, operation mechanism cabinet.

- Installation instructions drawings (including Support Structure drawings).

- Test records meet the requirements of IEC specification and standards.

- Certificates of quality management system, origin of products and accessories.

- Manufacturer's catalog and regulation of SF6 gas applicable in circuit breakers.

- The documentation, recommendations for implementation: packaging, transportation, installation, operation, inspection, maintenance of equipment and accessories, overhaul, periodic testing, reinforcement testing (such as frequency performance, content of work) ; common defects and how to deal with common failures.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Other requirements for circuit breakers

- Items not mentioned in the "Regulations on basic technical characteristics of 220 kV, 110 kV, circuit breakers on the power transmission grid" shall be applied according to the technical regulations of EVN, EVNNPT, TCVN standards, IEC or equivalent standard.

#### Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker

- The Bidder must to appoint at least 01 Circuit Breaker Professional of for Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker during install Circuit Breakers this package at outside (at 220kV Mong Cai substation). Circuit Breaker Professional  had to the manufacturer's training certificate or provide the authorization supervise for Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker.

- Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker according to 2878/EVNNPT-KT ngày 17/08/2018 doccument

#### Basic Data of 220 kV Circuit Breaker and 110 kV Circuit Breaker:

- Refer to Technical Data Sheet to have data of 220 kV Circuit Breaker and 110kV Circuit Breaker.

    - 22kV Circuit Breaker

#### General

- 22kV circuit breakers have the ability to close/open in normal operation mode and tripping in abnormal or fault operating modes of the power grid with voltage level of 22kV.

- Circuit breakers with common operating mechanism for 3 phases-circuit breaker, each phase has 01 arcing extinguish chamber with SF6 or vacuum; suitable for outdoor installation and operation.

- The circuit breaker is designed and manufactured in accordance with IEC 62271-100 or equivalent and technical specification referred to technical datasheet.

- Insulators of circuit breakers must be made in accordance with environmental conditions and specifications referred to technical datasheet.

- Circuit breakers shall be designed so that defective/damaged contact chambers and other components can be inspected and replaced quickly and easily.

- The circuit breaker design must ensure safety if there is an overvoltage of the switching operation or when a short circuit.

- Circuit breakers with isolated and arc extinguish by sulphur hexafluoride (SF6) gas insulated, must meet the requirements of SF6 gas system tightness with gas leakage ≤ 0.5%/year of the entire gas volume.

- SF6 gas or insulating and arc-extinguishing materials shall meet the detailed requirements in IEC 60376 standard. All materials used in the construction of SF6 circuit breaker shall be suitable for the working conditions in the atmosphere of SF6 gas and the decomposition products of SF6. The circuit breaker shall be able to withstand the maximum pressure during operation without gas leakage or deformation damage.

- The gas system of the tripping chamber must have gas pressure gauge and monitoring device to detect SF6 leakage at two levels. Alarm warning mode for SF6 gas density threshold at level 1 and lock control for SF6 gas density threshold at level 2 (lockout).

- The insulators of the circuit breaker pole posts shall be made according to IEC 62155 or equivalent. Porcelain insulators must have thermal, mechanical, electrical insulation, and operate in accordance with the environmental conditions and technical characteristics stated in technical datasheet.

#### Operating control cabinet

- Operating mechanism:

- Circuit breaker shall be equipped local control cabinet with operating mechanism, control switches and corresponding relays, switches, terminal clamp for control cables and other ancillary equipment.

- The operating control cabinet cover can be made of materials such as aluminum alloy, stainless steel or galvanized steel and can be painted on the surface of the cabinet to conform to the general specification; the operating control cabinet meet the minimum tightness IP 55.

- Operating mechanism and associated devices must be able to withstand impact forces according to IEC 62271-100 standard and have at least 10,000 operating sequences.

- Having open-close status indicator of circuit breaker for easy identification without opening the door of the cabinet.

- Equip the following equipment at the local control cabinet of the circuit breaker:

- Switch selection of LOCAL/REMOTE position (in which: Local: selects local operation; Remote: selects remote operation).

- Control switch On/Off operation in local: can use the self-return switch type or the “OPEN/CLOSE” push buttons.

- Counter of the number of closing - opening operations of the circuit breaker.

- Auxiliary contact system and limit switch to control the spring motor and alarm signal the status of spring storage.

- There is a spring charge status indicator: in the form of symbols/or letters to identify spring status of the circuit breaker is charged and not charged.

- The secondary terminal clamps must be extended at locations with multiple connections to prevent connecting multiple conductors in the same location. The number of spare at least 20% of the connected terminal. The clamp contacts must be designed firmly, not rusting during operation.

- Inside the control cabinet, there must be a common grounding copper rod, with locations for grounding connection.

- Operational requirements:

- Spring mechanism can be charged by manual and electric. In normal operation, the electric spring recharge shall begin immediately and automatically when the end of a closing cycle, the spring recharging time shall not exceed 15 second. The process of storing the spring is not interrupted until the spring is fully charged. If the spring is not fully charged, the closing circuit of the circuit breaker must be locked.

- Voltage supply of spring charge motor: 220VDC and recommended to use additional 220VAC power source.

- The circuit breaker shall have a device to prevent simultaneous remote control with local control. There is protective circuit for anti-switching continually, lockout, alarm circuits; signal circuit of error spring stored and motor protection circuit.

#### Installation arrangement

- Circuit breaker shall be designed to be suitable for direct mounting on hot-dip galvanized steel supports that coating thickness of not less than 80µm.

- In case the drive mechanism cabinet (control cabinet) of the circuit breaker is designed and installed with a height of more than 1.3 m above the ground, it must be attached with operator’s stand.

- Non-electric metal structures parts, equipment enclosures, operation mechansim cabinet must be directly earthed into the common grounding system of substation at the installation site.

#### Requirements for testing

- Routine test:

According to IEC 62271-100, including the following main items:

- Design and visual checks.

- Dielectric test on the main circuit.

- Test on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Tightness test.

- Mechanical operating tests.

- Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

The type test report shall be issued by the independent testing laboratories which are member of STL organization, according to IEC 62271-100, including the following main items:

- Dielectric test.

- Measurement of the resistance of the main circuit.

- Temperature rise tests.

- Short-time withstand current and peak withstand current tests.

- Additional tests on auxiliary and control circuits.

- Mechanical operation tests at ambient temperature (class M1).

- Short-circuits current making and breaking tests.

#### Accessories of circuit breaker

The circuit breaker must be equipped with the following accessories:

- Terminal clamp suitable for connecting conductor/bars and circuit breaker’s terminal.

- Bolts suitable for copper wire/grounding conductor.

- Bolts and nuts.

- Steel structure.

- Contact grease, lubricating grease, specialized paper for cleaning the contact surface, rubber gaskets.

#### Drawings and description, Technical documents:

The equipment shall be provided with the following drawings and technical documentation:

- General structure drawings.

- Principle drawing and internal connection of control cabinet, drive mechanism cabinet.

- Installation instructions drawings (including Steel structure drawings).

- Documentation for installation, operation, repair and maintenance of equipment, accessories.

- The documents recommend inspection, testing, maintenance, overhaul, how to handle common malfunctions and failures.

- Test reports and quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Other requirements for circuit breaker

- Circuit breaker is new 100%, no defects; certified origin (CO) is clear, legal; CB has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- Circuit breaker meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts) must be hot-dip galvanized according to TCVN 5408:2007 (and supplementary alternative documents), current equivalent standards for dip galvanizing.

- Allow unpacking and packing of individual parts for transporting and there is a table listing the number of equipment and material supplies in each package.

#### Basic Data of 22 kV Circuit Breaker

- Refer to Technical Data Sheet to have data of 22kV Circuit Breaker

      - DISCONNECTOR AND EARTHING SWWITCH

    - 220kV and 110kV Disconnectors and Earthing Switches

#### General

- Comply with the Technical standards of 220kV, 110kV outdoor Disconnectors and Earthing Switches in National Electricity of Vietnam issued together with the Decision No. 271/QD-EVN dated April 24, 2019 and No.91/QD-HDTV dated August 18, 2023 of Electricity of Vietnam and Decision No. 1676/QD-EVNNPT dated August 24, 2025 of National Power Transmission Corporation.

#### Definition of disconnectors for power transmission grid

- The disconnector for the power transmission grid is a device capable of participating in the high-voltage switching circuit in normal operating mode, only performing switching on the high-voltage circuit when there is no current or a smaller current the equipment's tolerance, creating a safe distance between live and non-energized parts. Disconnector on the power transmission grid must meet the durability of the climatic and environmental conditions in Vietnam: tropical, suitable for the environmental conditions of installation and operation of the substation.

- The basic standards for applying the design, manufacture and testing of disconnectors in power transmission grid are IEC 62271-102 and IEC 62271-1.

- For disconnectors with integrated electrical circuit breaking function, IEC 62271-108 standard is additionally applied.

#### General requirements on standards and environment

- All disconnector’s equipments on the power transmission grid that is manufactured and installed must meet Vietnamese regulations, standards, electricity industry standards, IEC/IEEE standards and be able to work stably long term under demanding working conditions, including Vietnam's natural climatic and environmental conditions.

- Environment conditions:

| Parameter | Request value |
| --- | --- |
| Altitude above sea level | : <1000 m |
| Climatic condition | : Tropical |
| Maximum air temperature | : 45°C |
| Minimum air temperature | : 0°C |
| Average air temperature | : 25°C |
| Maximum humidity | : 100% |
| Average humidity | : 85% |
| Creepage distance | : 31mm/kV |
| Seismic factor | : 0.15g |

- Depending on the natural conditions of the equipment installation location, as determined in QCVN 02:2009/BXD, the above environmental condition values may be changed to suit the actual requirements to be applied.

#### General requirements from power transmission systems

| Parameter | Unit | Request value |  |
| --- | --- | --- | --- |
| Normal Voltage | kV | 220 | 110 |
| Rated Frequency | Hz | 50 |  |
| Max operating voltage | kV | 242 | 121 |
| Min operating voltage | kV | 198 | 99 |
| Connection diagram |  | 3 phase, 3 wire |  |
| Method of neutral grounding |  | Directly grounded |  |
| Grounding touching coefficient of transmission grid |  | ≤ 1,4 |  |

#### Quality certificate requirements

- The manufacturer must have a certificate of the quality management system (ISO 9001:2015 or equivalent, still valid) applied to the production of the disconnector's component parts. The manufacturer must have a factory testing laboratory with certified testing equipments.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, labels for commercial and technical, etc.

##### Requirements for component parts of disconnector

- Disconnector

- 220 kV, 110 kV disconnectors installed on the power transmission grid are three phases or single phase, designed and manufactured in accordance with IEC 62271-102 standards so that they can be installed outside under the operating conditions of Vietnam's power transmission system. In addition to the IEC 62271-102 standard, the disconnector must meet the IEC 62271-1, IEC 60060 standards and must meet the requirements for insulation durable and temperature rise during long-term operation.

- Disconnectors are designed and manufactured to ensure safe operation under normal as well as fault conditions, to withstand atmospheric overvoltages, overvoltage phenomenon occurs when switching operation. The technical voltage requirements for disconnectors are clearly stated in technical datasheet.

- Depending on the installation location and working requirements of the disconnector, the required rated current for each disconnector is according to the values specified in the IEC 60059 standard but must not be less than the minimum value of 1250 A. The disconnector shall meet the long-term operating current and short-circuit current requirements specified in technical datasheet without exceeding the permissible operating temperature limits specified in IEC 62271-102.

- Disconnector must be properly designed and manufactured so that it cannot be opened or closed automatically by external forces. The safe distance for disconnectors in static position (static state) is specified in technical datasheet. In case of operation, if the distances between parts of the disconnector do not meet the safe distances in the static state, the equipment must ensure the insulation ability to withstand the power frequency voltage meets the voltage values for disconnectors equipped with earthing switches specified in technical datasheet.

- Disconnector must be properly designed and manufactured to enable easy inspection and prompt replacement of defective/damaged contacts and other parts. After assembly, the parts that make up the disconnector and the bracket must not create holes for birds to nest, which cause problems that affect the life of disconnector.

- The components of the disconnector must be designed and manufactured so that during operation under environmental conditions in the substation, overheating must not occur and must meet the requirements for temperature rise of the components parts of the disconnector specified in the standards IEC 62271-1:2017 and IEC 60137:2017.

- Disconnector with voltage levels of 220 kV and 110 kV are horizontal opening types. The disconnector can be operated by electric motor and/or by hand crank.

- Earthing switch

- The earthing switch attached to the disconnector is manufactured in accordance with IEC 62271-102 standards so that it can be installed outdoors under the operating conditions of Vietnam's power transmission system.

- Depending on the installation location and working requirements, each disconnector may be equipped 01 earthing switch or 02 earthing switch or without earthing switch. The earthing switch must meet the short-circuit withstand current requirements specified in technical datasheet without exceeding the permissible operating temperature limits as specified in standard IEC 62271-102.

- Disconnectors for transmission line with a length greater than 50 km or transmission line with multiple circuits operating in parallel, the earthing switch must be capable of switching electrostatically induced capacitive currents and electromagnetically induced currents with the values specified in Table 2 to meet the regulation according to IEC 62271-102.

- Earthing switch must be properly designed and manufactured so that it cannot be opened or closed automatically by external forces.

- The moving part of the earthing switch must be grounded to the disconnectors base by a soft copper wire or copper foil with a cross-section of not less than 50 mm2, ensuring it does not break or hinder the operation of earthing switch.

- Poles post of disconnector

- Pole post (supporting porcelain post) of disconnector must be made of non-assembled cylindrical porcelain, canopy circle, brown color according to IEC 60273 or equivalent. Porcelain must have thermal, mechanical and electrical durability, operate in accordance with the environmental conditions and technical characteristics listed in technical datasheet.

- Insulation porcelain of disconnector are manufactured to ensure that the distances from live parts to earth and between live parts comply with the requirements detailed in technical datasheet.

- Insulation porcelain of disconnector must be able to withstand the impact loads specified in detail in technical datasheet.

- Connection between of pole post and disconnector’s blade must be linked by bolts or welding to ensure no heat during long-term operation.

- Operating mechanism

- Operating mechanism and associated devices must be able to withstand impact forces according to IEC 62271-102 standard. Operating mechanism of disconnector must have safe mechanical switching at least 2000 times (equivalent to class M1). Operating mechanism of earthing switch must have safe mechanical switching at least 1000 times (equivalent to class M0).

- The contacts of the disconnector and earthing switch must be made of materials such as copper, copper alloy or silver/nickel plated aluminum alloy.

- The drive mechanism are made of non-corrosive, high-strength metal materials without rust, with an anti-skid lock.

- The drive motor circuit of the disconnector uses 220 VDC power source with voltage deviation (+10%; -15%) of rate voltage value. Motors must be equipped with overcurrent and overload protection.

- Drive mechanism cabinet, control cabinet

- Control cabinet can be integrated with the drive mechanism cabinet.

- Each disconnector must be equipped with local drive mechanism cabinet including the drive mechanism (can be use one drive mechanism cabinet for three-phase disconnectors), control lock, corresponding relays and switches, auxiliary contacts, limit contacts, clamps for control cables, LED lighting, drying resistors, power sockets, aptomat with auxiliary contacts, ventilation holes and other auxiliary equipment.

- Enclosure of mechanism cabinets and control cabinets can be made of aluminum alloy or stainless steel (Inox 304) or galvanized steel and the cabinet surface can be painted accordance to general technical requirements. The cabinet has a minimum thickness of 2 mm. The control cabinet must withstand extreme weather conditions, with a minimum degree of protection IP55. The cable ends coming into the cabinet must have cable-jacks of sizes suitable to the diameter of the cables, ensuring certainty for the cable ends and tightness for the cabinets.

- The mechanism cabinets is installed steady on a bracket structures to ensure not excessive vibration or abnormal phenomenon when operating disconnector and earthing switch, which can affect the life of disconnector.

- The mechanism cabinets of disconnector and earthing switch must be placed in a suitable position for does not affect the operator by arcing, and the operator can easily observe the movement contact during operation.

- The mechanism cabinets of disconnector and earthing switch equipped with the following parts:

- Selection switch of Local/Remote for position operating disconnector (in which: Local: select operate disconnector at local; Remote: select operate disconnector at remote).

- Close/Open switch for operating disconnector at local: can use self-return switching or "Open/Close" push buttons.

- Overcurrent and overload protection relays for the motor should be placed in the control cabinet.

- Auxiliary contact system and limit switch to control motor operation. Each DS/ES is equipped with auxiliary contact according to the status of the main DS/ES contact.

- The wiring terminals and connection terminals of the auxiliary contact block and limit switch in the mechanism/control cabinet must be made of stainless steel or metal treated to prevent rust. The secondary terminal must be able to expand at locations with many connections to limit the connection of many wires in same location. The number and technical requirements of auxiliary contacts must ensure compliance with the requirements stated in technical datasheet.

- The disconnector control circuit uses a 220 VDC power source with permissible voltage deviation (+10%; -15%).

- The drying and lighting circuits in the cabinet use a 220VAC power source with permissible voltage deviation (+10%; -15%).

- Inside control cabinet have common grounding copper rod with pre-drilled holes and attached nut bolts for grounding connection.

- Operation requirements

- The disconnector and earthing switch can be operated by manual and/or electrical to control close/open.

- Motor uses a 220 VDC voltage source.

- The disconnector must have a mechanism to prevent control in remote mode and local mode at the same time. Must have all circuits: electrical interlock circuit (interlock); motor error signal circuit; motor protection circuit; Non-synchronous signal circuit (for single-phase diaconnector/earthing switch), AC and DC power supply warning circuit for drying, lighting, motor, control circuit, ...

- DS/ES equipped with electrical and mechanical interlock (prohibited control to closing ES if DS side is energized) to prevent unwanted misoperation, ensure the safety of operators and equipment under operating conditions. In addition, the mechanical interlocks must operate reliably to avoid mechanical jamming when operate at the permissible electrical interlocking conditions.

- Operating mechanism force for DS or ES must not exceed 250N if only one rotation is required and not exceed 120N if multiple rotations are required (in case of manual operation) according to IEC 62271 -102.

- Requirement of secondary cable

- AC and DC power cables are provided with separate cables, cross-section not less than 2.5 mm2. Control and signal cables with a cross-section not less than 1.5 mm2. Secondary cables used copper cable with high quality, many fibers which water-resistant, fire-resistant, and the shielded to interference-proof.

- Installation arrangement

- Disconnector shall be suitably designed for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- The steel for the support is highly durable, withstands the loads of the disconnector and meets the requirements of the disconnector manufacturer. The cross-section of the support structures must be large enough to ensure not excessive vibration or abnormal phenomenon when operating disconnector and earthing switch, which cause problems that affect the life of disconnector.

- Steel parts (support structures, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 with coating thickness not less than 80 µm, the current standards for dip galvanizing, bolts and nuts.

- In case the operating mechanism cabinet (control cabinet) of the disconnector is designed and installed with a height of more than 1.3 m above the ground, it must be attached with operator’s stand.

- Non-electric metal structures parts, equipment enclosures, operation mechansim cabinet enclosures, control cabinets enclosures, etc. of the disconnector must be directly earthed into the common grounding system of substation. The grounding point of the disconnector must have the symbol "grounding", located at a convenient location to connect the grounding system of the substation. The cabinet enclosures and cabinet door are grounded with multi-strand copper wire with insulated sheath, the cross-section of the copper wire is not less than 1.5 mm2.

- Disconnector must be attached to the Parameter Table and the disconnector label is made of aluminum alloy or stainless steel (Inox 304), fully showing the main parameters of the disconnector according to IEC 62271-102. The data in the Parameter Table and the circuit breaker label must be highly durable, not lose color and always read clearly during the operation of the disconnector.

- During the installation process, must strictly follow the installation process, setting the disconnector according to the instructions of the manufacturer; use materials and accessories for DS to ensure quality, in accordance with the requirements of the manufacturer. The entire process of installing the disconnector must be carried out following sequence specified by the manufacturer.

- Accessories

Disconnector must be equipped with the following accessories:

- The terminal clamp suitable for connecting conductors/bars and terminal at HV side are made of aluminum alloy.

- Bolts and nuts made of stainless steel or hot-dip galvanized steel with a coating surface of not less than 80 μm, washers and anti-fall rings are included respectively.

- Bolts suitable for copper wire/grounding conductor.

- Structure and support of disconnector.

- Joint grease, lubricating grease, specialized paper for cleaning the contact surface.

- Specialized tools specific to disconnector: installation tools, manual tools for disconnector and earthing switch (Hand-wheel/operated lever).

- Other requirements

- Disconnector is new 100%, no defects;

- The manufacturer must commit the certified origin, certificate quality of goods, attach relevant documents and warranty the equipment according to current regulations commercial compliance as well as regulations on ensuring the technical life of equipment stated in item c - (The life requirements) of this Regulation.

##### The life requirements

The reliability as well as the life requirements of the disconnector are determined with the following minimum conditions:

- The number of safe mechanical switching operations is not less than 2000 times (equivalent to class M1) for disconnector.

- The number of safe mechanical switching operations is not less than 1000 times (equivalent to class M0) for earthing switch.

- Safe operating time before overhaul: at least 10 years or according to class M1 for disconnector, at least 10 years or according to class M0 for earthing switch (depending on condition comes first).

- Operating life for disconnector: minimum 25 years.

##### Requirements for testing

##### The manufacturer is responsible for providing complete documentation of the following:

- Supplied disconnectors shall be accompanied by adequate documentation demonstrating ability to meet the above technical specifications as well as IEC standards specified for each component of the equipment.

- Manufacturer and/or supplier of disconnectors is responsible for providing a full records, Type test, factory test (Routine test) demonstrating the ability to meet working requirements for supplied equipment, in which:

- The type test report shall be issued, or witness, or confirmed by the independent testing laboratories which are member of STL organization (Shorting Testing Liasion).

- The Routine Test reports are made and issued by the disconnector manufacturer.

##### Test requirements for disconnector:

Design, manufacture and testing comply with IEC 62271-102. The manufacturer must provide the following test documents:

Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

The type test report shall be issued by the independent testing laboratories or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025, according to IEC 62271-102, including the following main items:

- Dielectric tests.

- Measurement of the resistance of the main circuits.

- Continuous Current Test.

- Short time withstand current and peak withstand current tests.

- Mechanical endurance test.

For the following cases:

+	The 500 kV, 220 kV, 110 kV disconnectors have special requirements on installation location or purpose.

+	Special cases shall be decided by competent persons.

Then maybe require the manufacturer provide documents for proving partial or total compliance with the following types tests according to IEC 62271-102:

| No. | Test item | Condition | Equipment |  |
| --- | --- | --- | --- | --- |
|  |  |  | DS | DS |
| 1 | Test to verify the degrees of protection of enclosures | According to IP | x | x |
| 2 | Radio interference voltage RIV test | Ur ≥ Umax | x | x |
| 3 | EMC tests |  | x | x |
| 4 | Additional tests on auxiliary and control circuits | With auxiliary and control circuits | x | x |
| 5 | Operation during application of rated static mechanical terminal load |  | x | x |
| 6 | Extended mechanical endurance tests | For M1, M2 type | x | x |
| 7 | Low and high temperature tests | If the ambient temperature is greater than 40oC or less than -5oC | x | x |

Routine test report:

The manufacturer must provide documents of six routine tests according to IEC 62271-102 standards as following:

- Dielectric test on the main circuit.

- Tests on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Design and visual checks.

- Mechanical operating tests.

- Verification of earthing function (applies to DSs equipped with ES).

The manufacturer is responsible for providing a full records, routine test results of the above tests.

##### Requirements for transporting of disconnector

- Disconnector’s components is possible to remove or packing with a table listing the number of equipment and material supplies in each package for easily stored, transported by machine or manually, allowing re-installation and operation easily.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration, the impact of sea water, thunderstorms as well as other environmental influences.

##### Requirements for documents of disconnector

The manufacturer is responsible for providing complete documentation of the following:

- Table of required parameters for disconnector.

- Drawings describing the structure, dimensions and cross-sections of the main components of the equipment: disconnector, main blade, earthing blade, poles, operation mechanism cabinets, control cabinets, HV terminal, supporting structure; quantity, drawing, specification of accessories.

- Principle drawing and internal connection of control cabinet, operation mechanism cabinet.

- Installation instructions drawings (including support structure drawings).

- Test records meet the requirements of specification and IEC standards.

- Certificates of quality management system, origin of products and accessories.

- The documentation, recommendations for implementation: packaging, transportation, installation, operation, inspection, maintenance of equipment and accessories, overhaul, periodic testing, reinforcement testing (such as frequency performance, content of work); common defects and how to deal with common failures.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

##### Other requirements for disconnector

Items not mentioned in the "Regulations on basic technical characteristics of  220 kV, 110 kV disconnector on the power transmission grid" shall be applied according to the technical regulations of EVN, EVNNPT, TCVN standards, IEC or equivalent standard.

##### Basic Data of 220kV, 110kV Disconnector and Earthing switch

Refer to Technical Data Sheet to have data of 220kV, 110kV Disconnector and Earthing switch.

    - 22kV Disconnector and Earthing Switch

#### General

- Disconnector switch is the type using three phases, outdoor installation, two column center break type, comply with standards IEC 62271-102. Disconnector switch is horizontal opening type, which can be operated by hand-wheel or electrical motor. The mechanical mechanism of the disconnector switches must be designed so that the disconnector switches cannot close or open itself by external impulses.

- Earthing switch fitted with disconnector: 3-phase (corresponding to disconnector type), outdoor installation and comply with standards IEC 62271-102. The earthing switch can be operated by a lever, hand-wheel and electrical motor. The mechanical mechanism of the earthing switches must be designed so that the earthing switches cannot close or open itself by external impulses.

#### Operating control cabinet

- Operating mechanism:

- The drive mechanism and associated equipment must be able to withstand the impact forces according to IEC 62271-102.

- Disconnector must be equipped with a local operating control cabinet containing the operating mechanism, control lock and corresponding relays, switches, clamps for control cables and other auxiliary equipment. Connection clapms and connection clamps of  auxiliary and position contact block in operating and drive cabinet must be made of stainless steel or stainless treated metal.

- Drive cabinet cover can be made of materials such as aluminum alloy, stainless steel or galvanized steel and can be painted on the surface of the enclosure in accordance with the general specification, thickness ≥ 2mm, drive control cabinet is mounted on sturdy supporting, weatherproof, protection class IP 55.

- Having open-close status indicator of disconnector and earthing switch for easy identification without opening the door of the cabinet.

- Equip the following equipment at the local control cabinet of the disconnector:

- Switch selection of LOCAL/REMOTE position (in which: Local: selects local operation; Remote: selects remote operation).

- Control switch On/Off operation in local: can use the self-return switch type or the “OPEN/CLOSE” push buttons.

- The auxiliary contact system and the limit switch contact to control the motor. Each disconnector/earthing switches is equipped with auxiliary contacts according to the state of the disconnector/earthing main contact.

- Operational requirements

- Disconnector/earthing switches can operate on/off by manually and motor.

- Rate voltage of motor driver for DS and ES: 220VDC

- DS/ES equipped with electrical and mechanical interlock to prevent unwanted misoperation, ensure the safety of operators and equipment under operating conditions.

#### Installation arrangement

- Disconnector shall be designed to be suitable for direct mounting on hot-dip galvanized steel supports.

- Equipment must be equipped with details, grounding positions at all parts of non-charged steel structures, equipment cabinets, control cabinet,... to connect to the grounding system of substation.

#### Requirements for testing

- Routine test:

Disconnector shall be factory tested in accordance with IEC 62271-102 or equivalent standard comprising the following main items:

- Design and visual checks.

- Dielectric test on the main circuit.

- Test on auxiliary and control circuits.

- Measurement of the resistance of the main circuit.

- Mechanical operating tests.

- Verification of earthing function.

- Type test report:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

The type test report shall be issued by the independent testing laboratories or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025, according to IEC 62271-100, including the following main items:

- Dielectric tests;

- Measurement of resistance of the main;

- Continuous current test

- Short time withstand current and peak current withstand tests;

- Mechanical endurance test

- Extended mechanical endurance tests

#### Accessories of disconnector

- Terminal clamp for connecting.

- Bolts suitable for copper wire/grounding conductor.

- Bolts and nuts.

- Steel structure.

- Specialized join compound and paper for cleaning contact surfaces, rubber gaskets.

- Hand-wheel/operated lever to open and close DS and ES (if any) by manual.

#### Drawings and description, Technical documents

The equipment shall be provided with the following drawings and technical documentation:

- General structure drawings.

- Installation instructions drawings

- Principle drawing and internal connection of control cabinet.

- Documentation for installation, operation, repair and maintenance of equipment, accessories.

- The documents recommend inspection, testing, maintenance, overhaul, how to handle common malfunctions and failures.

- Test reports and quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Other requirements for DS

- Disconnector switch is new 100%, no defects; certified origin (CO) is clear, legal; has a certificate of quality; attach relevant documents to prove that the supplied goods comply with the design requirements and specified in the signed contract.

- Disconnector switch meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts) must be hot-dip galvanized according to TCVN 5408:2007, current equivalent standards for dip galvanizing.

- Allow unpacking and packing of individual parts for transporting and there is a table listing the number of equipment and material supplies in each package.

#### Basic Data of 22kV Disconnector and Earthing switch

- Refer to Technical Data Sheet to have data of 22kV Disconnector and Earthing switch.

Note:

- To ensure reliability of controlling, signaling and interlocking circuits of substation computerized control system  as well as reliability of busbar simulation circuit of busbar protections, the Disconnectors supplied shall be of high quality with best modern technology in design and manufacturing. The mechanical operating system shall be simple, easy of erection and adjustment, minimum of maintenance. The appropriate solutions shall be used to ensure the whole operating mechanism and transmission system of Disconnector and Earthing switches can operate securely, accurately and smoothly during all service lifetime.

- They shall be able to close and open whilst subjected to their rated mechanical terminal loads, plus wind loads acting on the equipment itself. HV main contacts shall securely lock in the closed position in such manner that they do not separate when subjected to the full rated short circuit current.

- Material of local control cubicle must be in Stainless Steel (Inox 304) or Aluminium Alloy (Al Mg3 H22).

- DS must be compliance with temperature-rise according to IEC 62271; IEC60137; vibration according to IEC 60068; IEC 60255; short circuit withstand according to IEC 62271-100,-1; insulation level according to IEC 62271; IEC 60137; IEC 60060.

- All Disconnector and Earthing switch (Designation HCB) from Siemens - India shall not be allowed for bid according to EVNNPT official document No. 3140/EVNNPT-KT+PC+ĐT+QLĐT+QLXD ngày 11/09/2019).

      - CURRENT TRANSFORMER

    - 220kV Current Transformers

#### General

- Current Transformers of 220kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1819/QĐ-EVNNPT dated September 16, 2025 of EVNNPT.

- The 220kV current transformer put into operation for power transmission grid is the type single phase, sealed type, Magnetic circuit and coil are placed on top of the current transformer, insulating oil, outdoor installation. Current transformer was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition			: Tropical

- Maximum air temperature		: 45°C

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum humidity		: 100%

- Average humidity			: 85%

- Seismic factor 			: 0.15g

- Creepage distance			: 31mm/kV

- Requirements of the electrical system installing the current transformer:

| Item | 220 kV system |
| --- | --- |
| Normal Voltage | 220 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 242 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |
| Grounding touching coefficient of transmission grid | ≤ 1,4 |

- Current transformer designed and manufactured meet working conditions comply with standards: IEC 60044-1 (2003-02); IEC 60815 (2008-10); IEC 60071-1 (2011-03); IEC 60137 (2008-07); IEC 61869-1 (2007-10); IEC 61869 -2 (2012-09); IEC 60060 (2010-11); IEC 60529 (2001-02); IEC 60296 (2012-02); IEC 60422 (2013-01); IEC 60028 (1925).

#### Requirement temperature rise, insulation strength, short current circuit

- The current transformer meet temperature rise requirement comply with standards: IEC 60137, IEC 61869-1, IEC 61869-2.

- The current transformer meet insulation strength requirement comply with standards: IEC 60137 and IEC 60060.

- The current transformer meet short current circuit requirement comply with standards: IEC 60044-1 and IEC 61869-2.

#### Reliability requirements

- Operation time until overhaul: ≥ 8 years.

- Total of operating time until to be replaced by a new CT: ≥ 20 years.

#### Requirements for component parts of current Transformers

- Requirements for winding coils of current transformers

- The coils are made of standard annealed copper at a temperature of 20 degrees celsius with resistivity no greater than [0.017241 (Ω.mm2/m); 0.15328(Ω.g/m)] comply with IEC 60028 (1925); Equivalent conductivity not less than 100% IACS.

- The quality insulating material is consistent with the insulation strength and temperature of CT.

- Insulation requirements between secondary windings: withstand voltage according to IEC 61869-2.

- Requirements for magnetic cores of current transformers

- The value of flexural dynamic force inflection point at rated frequency, when increased by 10% increases the excitation current by 50%.

- Residual magnetic coefficient for protective coils does not exceed 10%.

- Requirements for external insulation of current transformers

- Materials: Non-assembled cylindrical porcelain, canopy circle, brown color.

- Minimum creepage distance to meet the requirements of IEC 60815.

- Porcelain must have thermal, mechanical and electrical durability.

- Porcelain must be manufactured to meet the requirements of IEC 60137.

- Requirements for secondary terminal box of current transformers

- Material: Alloy or stainless steel, the thickness is not less than 1,5mm.

- Quantity of box: 01. For CT installed at metering points: secondary winding with accuracy level 0,2 and 0,5 for metering must be sealed for output of secondary winding.

- Cover box with gasket, hinge, lock handle. Terminal clamps is suitable for O-ring terminals for wires with a cross section of not less than 4 mm2.

- Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529.

- Cable ends entering boxes and cabinets must have cable termination connectors sized to match the diameter of the cable to ensure cable end robustness and tightness for boxes and cabinets (when there is no cable, these holes must be covered with a screw cap).

- Requirements for insulating oil

- The oil used in CT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

- The origin of oil, name, code and quantity of oil must be clearly stated in CT name plate.

- CT must be tight without leaking oil. Oil level indicator, oil sampling valve, oil drain valve, oil replenishment position.

- Mechanical requirements

- CT is capable of withstanding static loads according to table 7, standard IEC 61869-1, test time according to item 7.4.5, test diagram according to table 12, standard IEC 61869-1.

- Requirements for power arc

- The CT shall be able to withstand an internal arc in accordance with table 8, section 6.9, standard IEC 61869-1.

- Requirements for electromagnetic compatibility

- The level of radio frequency disturbance voltage generated within the CT shall comply with section 6.11, standard IEC 61869-1 (2007).

- The CT shall be capable of withstanding primary-to-secondary overvoltage with values ​​not exceeding the values ​​in table 9, standard IEC 61869-1 (2007).

#### General Arrangement

- Current transformers shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

- Unless otherwise stated, clearance from base of housing insullator to ground level must be at least 2250 mm.

#### Requirements for accuracy class

- For secondary windings having accuracy class 0.2 and 0.5: Current deviation, phase displacement measured at secondary windings at rated power (25% - 100%), with errors not exceeding values ​​in table 11 , standard IEC 60044-1 (or table 201, standard IEC 61869-2).

- For secondary winding with accuracy of class 5P: Current deviation, phase displacement measured at secondary winding at rated power (25% - 100%), there is an error not exceeding value in table 14 , standard IEC 60044-1 (or table 205, standard IEC 61869-2).

#### Requirements for specification sheet and label of current transformers

- Material made of stainless steel or oxidize. The handwriting is not faded during the life of current Transformers.

- The content on the parameter table can fully display the main current Transformers parameters according to IEC 60044-1, IEC 61869-2, IEC 61869-1.

#### Requirements for testing

- The Type Test, Special Type Test, Routine Test for current Transformers shall comply with requiremens according to IEC 60044-1, IEC 61869-1, IEC 61869-2 and submition all test report enclosred tested current Transformers. There must be test report for oil and current Transformers accessory testing.

#### Requirements for transporting of current transformers

- During transporting, it is do not not allow separate dismantling and packaging the components.

- Have solution to prevent moisture penetration and the impact of sea water.

#### Requirements for documents of current transformers

- Manufacturer information, summary of current Transformers specifications, origin of current Transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, current Transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of current Transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Requirements for testing

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

- The Short-circuit withstand capability test must by one member of STL organization, have name in the list following: Intertek (ASTA, implemented before May 22, 2024)-UK; CESI-Italy; CPRI-India; ESEF ASEFA-France; JSTC-Japan; KEMA-Netherland; KERI-South Korea; PEHLA-Germany; SATS-Norway; STLNA-USA; VEIKI-Hungary; ZKU-Czech Republic.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

Type test report:

The certificates required in according with IEC 60044-1, -2/IEC 61869-1, -2, including the following:

- Short-time current test;

- Temperature-rise test;

- Impulse voltage withstand test on primary terminals;

- Wet test for outdoor type transformers;

- Test for accuracy;

- Verification of the degree of protection by enclosures;

- Electromagnetic Compatibility tests.

Note: All tests have fully demonstrated the responsiveness of the equipment offered by bidder. The contractor may be rejected if does not meet the above requirements

- Routine Test:

Routine test is performed by the manufacturer on each product produced at the manufacturing facility. The routine tests are conducted in accordance with IEC 61869-1, -2 or TCVN 11845-2 or TCVN 7697-1 or equivalent standards, and include the following test items:

- Verification of markings

- Power - frequency withstand tests on primary terminals

- Power-frequency withstand test on secondary windings

- Power - frequency withstand test between sections

- Partial discharge measurement

- Inter-turn overvoltage test

- Test for accuracy

- Enclosure tightness at ambient temperature

- Measurement of capacitance and dielectric dissipation factor

- Measurement of capacitance and dielectric dissipation factor

The test items must be fully tested according to the standards specified in the dossier of requirements or with standards equivalent to the specified standards.

The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

#### Requirements for accessories of current transformer

- The CT using insulating oil, a oil sampling device is required for periodic testing in operation; must have spare oil in service of repair.

- Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

#### Requirements for transporting of current transformers

- During transporting, it is do not not allow separate dismantling and packaging the components.

- There is a table listing the number of equipment and material supplies in each package.

- Have solution to prevent moisture penetration and the impact of sea water

#### Requirements for documents of current transformers

- Manufacturer information, summary of current Transformers specifications, origin of current Transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, current Transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of current Transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Other requirements for current transformer

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

#### Basic Data of 220kV Current Transformer

- Refer to Technical Data Sheet to have data of 220kV Current Transformer

    - 110kV Current Transformer

- Current Transformers of 110kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 105/QD-HDTV dated September 21, 2021 of EVN.

#### Current Transformer type

- Single-phase, oil-immersed, vertical installation ensures outdoor operation and places with heavily polluted or saline environments, with full sealing position, for electrical measurement in neutral electrical systems direct grounding, rated voltage 110kV.

- The CT is designed, manufactured and tested to IEC 61869-1, IEC 61869-2 or equivalent standards, meeting the specifications in the specification sheet (110kV Curent Transformer datasheet).

- The secondary circuit side of the CT must be designed with a separate lead clamp sealing position for the metering coils (core) installed inside the terminal box of the CT.

#### Design and structure

- The CT primary coil is designed to operate with rated current and withstand the required fault current without damage. The CT is capable of withstanding current on the primary side when the secondary side is open circuited. At any open-circuit secondary winding with a terminal voltage in excess of 2.5kV, suitable voltage limiting protection should be provided.

- The CT secondary winding for measurement has a saturation characteristic that ensures that the connected measuring devices are not damaged by fault currents. CT ratio changes are performed on the secondary windings. The secondary winding terminals must be arranged in rows (measurement - protection) with symbols, markings and connected to the clamping blocks on the MK (Marshalling Kiosk) intermediate terminal or protection - control cabinet.

- CTs intended for protection shall fulfill the requirements for transient characteristics in accordance with the relevant standards.

- The terminal blocks of the secondary circuit used for measurement in the terminal block of the CT shall be designed separately from the secondary circuit for protection and shall have a separate lead clamp sealing position for the terminal rows of secondary circuit wire used for this measurement.

- Terminal boxes shall be constructed of aluminum or aluminum alloy or stainless steel that are weather resistant and have a minimum sealing degree of IP55.

#### General Arrangement

- The current transformer is suitable for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- Each current transformer must be supplied with suitable pole clamps for connection to the conductor cross-sections used.

- Each current transformer must have details, grounding positions at all non-live metal structural parts for connection to the grounding system of the substation.

- Current transformers shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

#### Requirements for testing

### Routine Test

- Routine test is performed by the Manufacturer on each product manufactured at the Manufacturer. Factory testing is performed according to IEC 61869-1, IEC 61869-2 or equivalent standards, including the following test items:

- Verification of markings;

- Power - frequency withstand tests on primary terminals;

- Power-frequency withstand tests, between sections;

- Power-frequency withstand test on secondary windings;

- Partial discharge measurement;

- Inter-turn overvoltage test;

- Test for accuracy;

- Enclosure tightness at ambient temperature;

- Measurement of capacitance and dielectric dissipation factor;

### Type test

- Type testing must be performed and certified by an independent test laboratory certified to ISO/IEC 17025 and must be a member of the Society for Short Circuit Testing (STL) on similar product samples. Type testing is carried out according to IEC 61869-1, IEC 61869-2 or equivalent standards, including the following test items:

- Short-time current test;

- Temperature-rise test;

- Impulse voltage withstand test on primary terminals;

- Test for accuracy;

- Wet test for outdoor type transformers;

- Verification of the degree of protection by enclosures;

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements.

#### Drawing and Technical document

- Equipment shall be provided with the following drawings and technical documentation:

- An overview drawing of the size, mass, and bearing capacity of the current transformer.

- Drawing depicting the structure.

- Installation instructions drawings (including equipment bracket drawings).

- Principle drawing and connection of the second terminal block.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Sample approval certificate

- The equipment must be certified by the Vietnam General Administration for Standards, Metrology and Quality (STAMEQ) for sample approval.

#### Other requirements:

- Equipment is 100% brand new, no defects with full certifications of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements. in accordance with the requirements of the design and the provisions of the signed contract.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 and current equivalent standards on hot-dip galvanizing. The coating thickness should not be less than 80µm.

#### Basic Data of 110kV Current Transformer

- Refer to Technical Data Sheet to have data of 110kV Current Transformer

Note: For 110kV current transformers, it is necessary to design a location for sealing and lead clamping separately for the measuring circuit serving the measurement of the boundary point of electricity trading between EVNNPT and EVNNPC

    - 22kV Current Transformer

#### General

- Current Transformer (CT - Current Transformer) of the single-phase type, solid or liquid insulation (insulating oil), for outdoor or indoor installation, rated voltage 22 kV.

- For solid insulation CT, the insulating material must be made of epoxy resin (Epoxy resin), with good mechanical and electrical properties, able to withstand sudden temperature changes, and UV resistant. CT casting technology must be vacuum casting (vacuum cast) or pressure casting (APG) technology for epoxy insulation.

- For oil-insulating CTs: The insulators must be glazed ceramics capable of working in heavily polluted conditions such as coastal areas, salt mist, industrial pollution, ultraviolet radiation, etc. as well as a humid tropical climate. The CT tank shell must be made from bearing steel, protected against rust and corrosion by electrostatic painting technology with a minimum coating thickness of 80µm. Insulating oil used for CT must be specifically used for transformers, without PCB.

- Current transformers are designed and tested in accordance with IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 or equivalent standards, meeting the parameters in the table of description. specification description (22kV Current Transformer datasheet).

- Current transformers are designed using environmentally suitable insulating materials according to IEC 60815 - Guidelines for the selection of insulating materials with respect to pollution conditions.

- The primary terminals are made of tin-plated or nickel-plated copper alloy to ensure connection to copper conductors whose rated current corresponds to the primary current of the current transformer.

- The secondary terminals are located in the surface mount terminal block of the body. The secondary terminals are made of brass. Terminal box constructed of aluminum or aluminum alloy or stainless steel or hot-dip galvanized steel, resistant to changes in weather and with location for separate lead clamp sealing for measuring coils.

- Current transformers for protective functions shall fully satisfy the requirements for transient characteristics in accordance with the relevant standards.

- Current transformers are equipped with accessories, clamping terminals, together with bolts, nuts, washers suitable for aluminum wire, copper wire and wire cross section according to the design.

#### Installation arrangement

- The current transformer is designed to be suitable for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- Each current transformer must be equipped with earthing pole and allowed to connect to the main earthing grid for safety working purpose.

- Non-energetic metal structural parts of the current transformer must be grounded directly to the grounding system at the equipment installation location.

- The connection box must be able to withstand weather changes and have a protection level of IP55.

#### Requirements for testing

### Routine test

- The Routine Test for current Transformers shall comply with requirements according to IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 or equivalent, including the following test items:

- Verification of makings.

- Power-frequency voltage withstand test on primary terminals

- Power-frequency voltage withstand test on secondary terminals

- Power-frequency voltage withstand test between sections

- Partial discharge measurement

- Inter-turn overvoltage test

- Tests for accuracy

### Type Test:

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

- Type test must be performed and certified by an independent test laboratory certified to ISO/IEC 17025 on similar product samples. Type test is carried out according to IEC 61869-1, IEC 61869-2 or TCVN 11845-2 or TCVN 7697-1 equivalent standards, including the following test items:

- Short-time current test.

- Temperature-rise test.

- Impulse voltage withstand test on primary terminals.

- Test for accuracy.

- Wet test for outdoor type transformers.

- Verification of the degree of protection by enclosures.

- For solid insulation CTs, in addition to the above test items, the equipment shall be additionally tested item “Insulation aging test under UV radiation” according to ASTM D4587 or IEC 62217 or equivalent standards. Testing by an independent laboratory on a similar product sample.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements.

#### Requirements for drawings and technical documents

The equipment shall be provided with the following drawings and technical documentation:

- Overview drawing of the size, mass

- Drawing depicting the structure.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Sample approval certificate

- The equipment must be certified by the Vietnam General Administration of Standards, Metrology and Quality (STAMEQ) for sample approval.

#### Other requirement

- Equipment is 100% brand new, no defects with full specifications certification of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements of the design and specified in the contract signed.

- Equipment meet durability to climatic and environmental conditions in Vietnam; tropicalized, suitable for the conditions of the installation and operating environment.

- Steel components (posts, beams, brackets, grounding, bolts, nuts, etc) must be hot-dip galvanized according to TCVN 5408:2007 and current equivalent standards on hot-dip galvanizing.

#### Basic data for 22kV current transformer

- Refer to Technical Data Sheet to have data of 22kV Current Transformer.

      - VOLTAGE TRANSFORMER

    - 220kV Capacitor voltage transformer

#### General

- Capacitor Voltage Transformers of 220kV according to the basic technical specification of transmission grid equipment, issued under Decision No. 1816/QĐ-EVNNPT dated September 16, 2025 of EVNNPT.

- The capacitor voltage transformer, TRV capacitor, put into operation for power transmission grid is the type single phase, sealed type, capacitor voltage transformer type (TRV capacitor type), insulating oil, outdoor installation. Capacitor voltage transformer (TRV capacitor) was designed and manufactured by material and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- Environment conditions:

- Altitude above sea level		: <1000 m

- Climatic condition			: Tropical

- Maximum air temperature		: 45°C

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum humidity		: 100%

- Average humidity			: 85%

- Seismic factor 			: 0.15g

- Creepage distance			: 31mm/kV

- Requirements of the electrical system installing the capacitor voltage transformer:

| Item | 220 kV system |
| --- | --- |
| Normal Voltage | 220 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 242 kV |
| Rated withstand short current capacity | 50 kA |
| Rated duration of short-circuit | ≥ 1s |
| Grounding touching coefficient of transmission grid | ≤1,4 |

- Voltage transformer is designed and manufactured meet working conditions comply with standards: IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60815, IEC 60071, IEC 60137 (2008), IEC 60358-3 (2013)

#### Requirement temperature rise, insulation strength, vibration, short current circuit

- The voltage transformer meet temperature rise requirement comply with standards: IEC 60044-2, IEC 60044-5, IEC 61869-5, IEC 60137.

- The voltage transformer meet vibration requirement comply with standards: IEC 60068, IEC 60255.

- The voltage transformer meet insulation strength requirement comply with standards: IEC 60071-1, IEC 60060-1, IEC 60137, IEC 61869-5.

- The voltage transformer meet short current circuit requirement comply with standards: IEC 60044-2 and IEC 61869-5, IEC 60060-1.

#### Reliability requirements

- Operation time until overhaul: ≥ 8 years.

- Total of operating time until to be replaced by a new CVT: ≥ 20 years.

#### Requirements for component parts of capacitor voltage transformer

- Requirements for capacitor type divider

- Each capacitor floor is an unconnected solid block with an insulated porcelain cover.

- Each capacitor floor has an oil level indicator.

- Requirements for the electromagnetic unit

- Case made of metal material does not corrode and rust.

- Intermediate transformer: insulated copper coil.

- There is inductance reactor coil with inductance according to section 3.1.537, standard IEC 61869-5.

- There is damping device: overvoltage limit, prevent ferromagnetic resonance and temporary impacts.

- There is a earthing switch.

- There is discharge coils capable of continuous operation with current 1A, withstand short-circuit currents 50 A for 0.2s according to section 6.504.2 standard IEC 61869-5.

- There is voltage limiting elements according to section 6.504.3 of IEC 61869-5 standard.

- There is oil drain valve, oil sampling valve, earth switch, lightning protection, oil level indicator.

- There is capacitance measurement positions C1, C2.

- The electromagnetic unit must be able to withstand lightning impulse voltages (peak values): ≥ Ulightning impulse voltages x C1/ (C1+C2)

- The electromagnetic unit must be able to withstand short-term industrial frequency voltages (r.m.s.): ≥ UPrimary rated of CVT x 3.3x C1/ (C1+C2)

- Requirements for secondary terminal box of capacitor voltage transformers

- Material: Alloy or stainless steel. box with lid, located for sealing lead seals.

- Quantity of box: 01.

- Cabinets must be made to meet the minimum tightness IP 55 according to IEC 60529. Cable terminals come into cabinet must have suitable union with diameter and ensure the strengtheness for terminal and tighness of cabinet.

- Requirements for external insulation of capacitor voltage transformers

- Each capacitor voltage transformers divider, materials cylindrical ceramic porcelain, canopy circle, brown color.

- Porcelain must have thermal, mechanical and electrical durability. Porcelain must be manufactured to meet the requirements of IEC 60137.

- The capacitor must be compely with IEC 60050-151, IEC 60050-436.

- Requirements for insulating oil

- The oil used in CVT is an antioxidant oil, free of PCBs or other hazardous substances. The list of additives in oil must be published according to IEC 60296 (2012). Oil must be able to blend properly with Shell, Nynas.

- The origin of oil, name, code and quantity of oil must be clearly stated in CVT name plate.

- Requirement for CVT intermediate cabinets

- Manufacturing materials: aluminum alloy or stainless steel. Number of cabinets: 01 cabinets/3 CVT.

- In the cabinet, there must be sufficient accessories (circuit breaker, clamps, lighting leds, sockets ...) for: 3-phase combination of CVT, putting or separating each phase of CVT from operation.

#### Requirement for ferromagnetic resonance

- The voltage transformer shall meet the value of ferromagnetic resonance according to Table 7a, standard IEC 60044-5.

- The voltage transformer shall meet the value of ferromagnetic resonance according to Table 506, Section 6.502 and test according to Table 512, standard IEC 61869-5.

#### Requirements for accuracy class of capacitor voltage transformers

- For secondary windings having accuracy class 0.2, 0.5: Voltage error and angle of phase difference must not exceed the value in Table 11, IEC 61869-5 standard.

- For secondary winding with accuracy of class 3P: Voltage error and angle of phase difference must not exceed the value of Table 502, IEC 61869-5 standard.

#### Requirements for grounding connection

- The neutral grounding point of CVT must arranged in a position convenient for grounding with the system's earthing system.

- The intermediate connection cabinets: The interior must have a common copper ground bar arranged with available drill holes and sufficient.

#### Requirements for specification sheet and label

- Material made of stainless steel.

- The content on the parameter table can fully display the main capacitor voltage transformers parameters according to IEC 60044-2-5. The handwriting is not faded during the life of voltage Transformers. Capacitive voltage transformer according to section 6.13.501, IEC 61869-5.

#### Requirements for testing, checking, installing, maintenance

- The Type Test, Special Type Test, Routine Test for capacitor voltage transformers shall comply with requiremens according to IEC 60044-2, -5 and submition all test report enclosred tested voltage Transformers. Capacitive voltage transformer according to Table 10, section 7, IEC61869-5.

- The CVT manufacturer shall have a detailed technical procedure guiding the installation, maintenance, repair, overhaul and testing of CVT in operation (according to IEC 61869-1). There are instructions for oil sampling and adding oils.

#### Requirements for transporting of capacitor voltage transformers

- During transporting, it is do not not allow separate dismantling and packaging the components.

- Have solution to prevent moisture penetration and the impact of sea water.

#### Requirements for documents of capacitor voltage transformers

- Manufacturer information, summary of voltage transformers specifications, origin of voltage transformers accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, voltage transformers structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of voltage transformers.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- There are instructions for oil sampling and adding oils. Assess the quality of oil.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Requirements for testing Capacitor Voltage Transformers

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025.

- The Short-circuit withstand capability test must by one member of STL organization, have name in the list following: Intertek (ASTA, implemented before May 22, 2024)-UK; CESI-Italy; CPRI-India; ESEF ASEFA-France; JSTC-Japan; KEMA-Netherland; KERI-South Korea; PEHLA-Germany; SATS-Norway; STLNA-USA; VEIKI-Hungary; ZKU-Czech Republic.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

Type test:

- Type tests must be performed on a sample of a similar product. The certificates required in according with IEC 61869-1,3,5, including the following:

- Short – Circuit withstand capability test.

- Temperature - rise test;

- Capacitance and tan measurement at power-frequency.

- Impulse voltage withstand test on primary terminals;

- Chopped impulse test;

- Accuracy tests.

- Wet test for outdoor type transformer;

- Verification of the degree of protection by enclosures;

- Enclosures tightness test at ambient temperature;

- Ferro-resonance test;

- Electromagnetic Compatibility tests;

- Transient response test (for protective capacitive transformers).

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements.

- Routine tests:

- Routine test is performed by the Manufacturer on each product manufactured at the Manufacturer. The following routine tests shall be carried out at the factory for each type of voltage transformer:

- Construction (general) inspection.

- Verification of markings.

- Power frequency withstand test on the primary terminals;

- Power frequency withstand test on secondary terminals;

- Power frequency withstand test between sections;

- Partial discharge test.

- Ferro-resonance check;

- Tests for accuracy.

- Enclosures tightness test at ambient temperature;

- Measurement of capacitance and dielectric dissipation factor.

- The test items must be fully tested according to the standards specified in the dossier of requirements or with standards equivalent to the specified standards.

- The certificate of approval of samples, the certificate of verification of measuring devices, issued by the Vietnam Standards and Quality Center.

#### General Arrangement

- Voltage transformers shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

- Unless otherwise stated, clearance from HV terminal to ground is approximately 5300mm for 245kV capacitive voltage transformer. Clearance from base of housing insullator to ground level must be at least 2250 mm.

#### Requirements for accessories of Capacitor voltage Transformers

- The CVT using insulating oil, a oil sampling device is required for periodic testing in operation; must have spare oil in service of repair.

- Terminal clamps with specifications suitable for high voltage terminals of circuit breaker, terminal at HV side use type not less than 6 bolts.

#### Basic Data of 220kV Capacitor Voltage Transformer

- Refer to Technical Data Sheet to have data of 220kV Capacitor Voltage Transformer.

Note: All 220kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 220kV CVT (WP 245 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021;

    - 110kV Capacitor Voltage Transformer

#### Capacitor Voltage Transformer type

- It is a single-phase capacitor voltage transformer (CVT), using oil-impregnated paper, installed vertically to ensure outdoor operation and where there is a heavily polluted or salty environment, with full sealing position, used for measurement. electricity in an electrical system with a directly earthed neutral, rated voltage 110 kV.

- CVT is designed and manufactured according to IEC 61869-1, IEC 61869-5 or equivalent standards, meeting the specifications in the specification table (Datasheet).

- The secondary circuit side of the CVT must be designed with a separate lead clamp sealing position for the metering coils (core) installed inside the CVT junction box.

- 110kV voltage transformer according to Technical Standards for 22, 35 and 110 kV voltage transformers applied in Vietnam National Electricity Group, issued together with Decision No. 104/QD-EVN dated September 21, 2021. The standard number is: TCCS 07:2021/EVN.

#### Design and Structure

- CVTs used for protection shall fulfill the requirements for transient characteristics in accordance with the relevant standards.

- The secondary windings must be arranged in rows (measurement - protection) with symbols, markings and connected to the clamping blocks on the MK (Marshalling Kiosk) intermediate terminal or the security control cabinet.

- The terminal blocks of the secondary circuit for measurement in the terminal block of the CVT shall be designed separately from the secondary circuit for protection and shall have a separate lead clamp sealing position for the terminal rows. secondary circuit wire used for this measurement.

- Terminal boxes shall be constructed of aluminum or aluminum alloy or stainless steel that are weather resistant and have a minimum sealing degree of IP55.

#### Installation arrangement

- CVT is suitable for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- Each CVT must be supplied with suitable pole clamps for connection to the conductor cross-sections used.

- Each CVT must have details, grounding positions at all non-live metal structural parts for connection to the grounding system of the substation.

- CVT shall be suitable for mounting directly on concrete pads and shall include any necessary supporting steel structure. All fixing bolts shall be provided by Purchaser.

#### Test requirements

        - Routine test

- Routine test is performed by the Manufacturer on each product produced at the Manufacturer. Factory testing is performed according to IEC 61869-1, IEC 61869-5 or equivalent standards, including the following test items:

- Verification of markings;

- Power frequency voltage withstand test on primary terminals:

- Power frequency voltage withstand test on secondary terminals;

- Power frequency voltage withstand test between sections;

- Partial discharge measurement;

- Test for accurracy;

- Ferro - resonance check;

- Enclosure tightness test at ambient temperature;

        - Type test

- Type testing must be performed and certified by an independent test laboratory certified to ISO/IEC 17025 and must be a member of the Society for Short Circuit Testing (STL) on similar product samples. Type testing is carried out according to IEC 61869-1, IEC 61869-5 or equivalent standards, including the following test items.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

- Short-circuit withstand capability test

- Temperature-rise test.

- Capacitance and tanδ measurement at power-frequency

- Impulse voltage withstand test on primary terminals.

- Chopped impulse test.

- Test for accuracy

- Ferro – resonance test.

- Wet test for outdoor type transformers

- Verification of the degree of protection by enclosures

- Enclosure tightness test at ambient temperature;

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements.

#### Drawing and Technical document:

- Equipment shall be provided with the following drawings and technical documentation:

- An overview drawing of the size, mass, and bearing capacity of the CVT.

- Drawing depicting the structure.

- Installation instructions drawings (including equipment bracket drawings).

- Principle drawing and connection of the second terminal block.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Sample approval certificate

- The equipment must be certified by the Vietnam General Administration for Standards, Metrology and Quality (STAMEQ) for sample approval.

#### Other requirements:

- Equipment is 100% brand new, no defects with full certifications of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements. in accordance with the requirements of the design and the provisions of the signed contract.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 and equivalent standards on hot-dip galvanizing. The coating thickness should not be less than 80µm.

#### Basic Data of 110kV CVT

- Refer to Technical Data Sheet to have data of 110kV CVT

Notes: All 110kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 110kV CVT (WN 145 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021.

For 110kV CVT, it is necessary to design a location for sealing and lead clamping separately for the measuring circuit serving the measurement of the boundary point of electricity trading between EVNNPT and EVNNPC

    - 22kV Voltage transformer

- 22kV voltage transformer according to Technical Standards for 22, 35 and 110 kV voltage transformers applied in Vietnam National Electricity Group, issued together with Decision No. 104/QD-EVN dated September 21, 2021.

#### General Requirements

- Voltage transformers (VT) of single phase, solid insulating material or liquid insulation (insulating oil), for outdoor or indoor installation, rated voltage 22kV.

- For solid insulating VT, the insulating material must be made of epoxy resin (Epoxy resin), with good mechanical and electrical properties, able to withstand sudden temperature changes, and UV resistant. VT casting technology must be vacuum casting technology (vacuum cast) or pressure casting technology (APG) for epoxy insulation.

- For oil insulators VT: The insulators must be glazed ceramics capable of working in heavily polluted conditions such as coastal areas, salt mist, industrial pollution, ultraviolet radiation, etc. as well as a humid tropical climate. VT tank shell must be made from bearing steel, protected against rust and corrosion by electrostatic painting technology with a minimum coating thickness of 80µm. Insulation oil used for VT must be the oil specifically used for transformers, without PCB.

- Voltage transformers are designed and tested according to IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent standards, meeting the parameters in the table of description specification description (Datasheet of 22kV VT);

- Voltage transformers are designed using environmentally suitable insulating materials according to IEC 60815 - Guidelines for the selection of insulating materials with regard to contamination conditions.

- The secondary terminals are located in the surface mount terminal block of the body. The secondary terminals are made of brass. Terminal boxes are constructed of aluminum or aluminum alloy or stainless steel, are weather resistant and have a location to seal separate lead clamps for the measuring coils.

- Voltage transformers for the protective function shall fully satisfy the requirements for the transient function in accordance with the relevant standards.

- The voltage transformer is equipped with accessories, clamps with bolts, nuts, washers suitable for aluminum wire, copper wire and wire cross-section according to the design.

#### Installation Arrangement

- Voltage transformers shall be suitably designed for direct mounting on hot-dip galvanized steel supports with a coating thickness of not less than 80µm.

- Each Voltage transformer must have grounding terminals, allowing connection to the main earthing system for safety and working purposes.

- The non-live metal structural parts of the current transformer must be grounded directly into the grounding system at the equipment installation location.

- The junction box must be weatherproof, with a degree of protection IP55.

#### Test Requirement

        - Routine test

- Routine test is performed by the Manufacturer on each product manufactured at the Manufacturer. Routine test is carried out in accordance with IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent standards, including the following test items:

- Verification of markings;

- Power - frequency withstand tests on primary terminals;

- Power-frequency withstand test on secondary windings;

- Power-frequency withstand tests between sections;

- Partial discharge measurement;

- Test for accuracy;

- Inter-turn overvoltage test.

        - Type test

- Type testing shall be performed and certified by an independent testing laboratory (ISO/IEC 17025 certified) on a similar product sample. Type testing is carried out in accordance with IEC 61869-1, IEC 61869-3 or TCVN 11845-3 or TCVN 7697-2 or equivalent standards, including the following test items:

- Short-time current test;

- Temperature-rise test;

- Impulse voltage withstand test on primary terminals;

- Test for accuracy;

- Wet test for outdoor type transformers;

- Verification of the degree of protection by enclosures;

- For solid-insulated VTs, in addition to the above test items, equipment shall be additionally tested under the category “Insulation aging test under UV radiation” according to ASTM D4587 or IEC 62217 or equivalent.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors will be rejected if does not meet the above requirements.

#### Drawings and Technical documents:

- Equipment shall be provided with the following drawings and technical documentation:

- An overview drawing of the size, mass, and bearing capacity of the Voltage transformer.

- Drawing depicting the structure.

- Installation instructions drawings (including equipment bracket drawings).

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- Test records and ISO quality management certificates

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Sample approval certificate

- The equipment must be certified by the Vietnam General Administration for Standards, Metrology and Quality (STAMEQ) for sample approval.

#### Other requirements:

- Equipment is 100% brand new, no defects with full certifications of clear, legal origin and certification of goods quality, together with other relevant documents proving that the equipment meets the requirements. in accordance with the requirements of the design and the provisions of the signed contract.

- Equipment must meet durability for climatic and environmental conditions in Vietnam: tropicalized, suitable for operating environment conditions.

- Steel parts (pillars, beams, brackets, grounding, bolts, nuts, etc.) must be hot-dip galvanized according to TCVN 5408:2007 and current equivalent standards on hot-dip galvanizing.

#### Basic Data of 22kV Voltage Transformer

- Refer to Technical Data Sheet to have data of 22kV Voltage Transformer.

      - SURGE ARRESTER

    - 220kV Surge Arrester

#### General

      - General conditions

220kV Surge Arresters  according to the basic technical specification of transmission grid equipment, issued under Decision No. 1158/QD-EVNNPT dated June 26 2025 of EVNNPT and Decision No. 2416/QD-EVNNPT dated December 09, 2025 of EVNNPT.

The installation of surge arresters (CSV) at transmission substations must comply with Vietnamese regulations, national standards, and power industry standards, be tropicalized, and capable of stable and long-term operation under the environmental conditions of installation and operation at transmission substations, including natural climatic conditions.”

Environment conditions:

Altitude above sea level		: <1000 m

Climatic condition			: Tropical

Maximum air temperature		: 45°C

Minimum air temperature		: 0°C

Average air temperature		: 25°C

Maximum humidity		: 100%

Average humidity			: 85%

Maximum ground acceleration	: 0,22xg

Averag wind speed			: 2m/s

Creepage distance			: 31mm/kV

- Depending on the natural conditions of the equipment installation location, as determined in QCVN 02:2022/BXD, the above environmental condition values may be changed to suit the actual requirements to be applied.

Information for installation place

| Item | 220 kV system |
| --- | --- |
| Normal Voltage | 220 kV |
| Rated Frequency | 50 Hz |
| Max operating voltage | 242 kV |
| Min operating voltage | 198 kV |
| Connection diagram | 3-phase 3-wire |
| Neutral grounding mode | Direct |
| Ground fault factor of transmission grid | ≤1,4 |

      - Quality certificate requirements:

- The manufacturer must have a certificate of the quality management system (ISO 9001:2015 or equivalent, still valid) applied to the production of the surge arrester component parts. The manufacturer must have a factory testing laboratory with certified testing equipments.

- Manufacturers must comply with Vietnam's regulations on energy saving, environment, intellectual property, labels for commercial and technical, etc

    - Requirements for component parts of surge arrester

      - Surge arrester

- Surge arresters (SA) for 220kV substations shall be single-phase, gapless type, applied for phase-to-earth protection. For neutral protection or longitudinal overvoltage protection of equipment, separate operating conditions of the surge arrester must be calculated and parameters must be selected accordingly.

- Surge arresters (SA) for transmission substations shall be designed, manufactured, and tested for outdoor installation and continuous operation. The surge arresters must meet the requirements for insulation strength and temperature rise during long-term operation

- The structure and main components of the surge arrester (SA) include:

- SA housing and SA core;

- SA base insulator (depending on the case);

- Leakage current meter, Surge counter, accessories, and connecting conductors from the surge arrester to the common earthing system of the substation.

- The housing and core of the surge arrester (CSV) may be manufactured in multiple layers (multiple elements) firmly connected together to ensure mechanical strength throughout the processes of transportation, installation, operation, and maintenance of the surge arrester.

- The core of the surge arrester consists of non-linear resistors using metal oxide (MO) of ZnO type. MO has low resistance when overvoltage occurs and high resistance at the rated operating voltage of the power system.

- All parts of the surge arrester must be designed and manufactured so that, during operation under substation environmental conditions, no overheating occurs, and they must comply with the requirements on temperature rise of surge arrester components as specified in manufacturing standards.

- The surge arrester (CSV) must ensure mechanical strength, without cracks, fractures, or degradation; it must withstand the effects of the substation environment and electric field, the impacts that may occur in case of transmission line/substation faults, as well as the effects of atmospheric overvoltages and switching overvoltages.

- The surge arrester must be designed and manufactured so that, during installation, it does not violate the requirements for phase-to-earth and phase-to-phase clearances as specified in the Electrical Equipment Regulations and Safety Regulations for substations.

      - Surge Arrester Housing

- The surge arrester (CSV) housing shall be made of porcelain or polymer (silicone rubber) material, reinforced with load-bearing materials.

- For surge arresters with porcelain housings:

- The housing shall be structured as a sealed chamber and capable of releasing internal pressure through a pressure relief valve when the arrester operates under conditions exceeding its design capability.

- The pressure relief valve must ensure the tightness of the sealed arrester housing, preventing moisture ingress.

- For surge arresters with polymer housings:

- The polymer housing together with the arrester core shall be constructed to ensure the required mechanical strength (e.g., reinforced with fiberglass rods, load-bearing insulating rods, etc.), resistant to bending and torsion, and shall not deform or tilt under the load of connecting conductors.

- The housing material shall withstand natural environmental factors such as: water resistance, fungus resistance, dust resistance, acid resistance, crack resistance, resistance to solar radiation and ultraviolet (UV) rays, anti-aging properties, and capability of operating under conditions of salt fog, industrial pollution, coastal areas, and regions with high lightning density.

- The housing shall not discolor or develop stains, nor allow moss, fungus, or mold to appear during operation. The housing and external insulating sheds shall not be damaged by tearing or impact, and shall not crack or degrade due to environmental or electrical field stresses.

- The surge arrester housing must comply with insulation requirements for equipment at the corresponding voltage level as specified by withstand voltage values, creepage distance of the insulation, and the ability to withstand short-circuit currents that may occur at the substation. These values are specified in Table 2, Article 7, and may be adjusted depending on the installation location of the surge arrester within the power system.

- The surge arrester housing must be capable of withstanding static and dynamic forces that may act on the arrester, as calculated and determined by the consultant in the design documentation, or as additionally required in the procurement documents, in accordance with the arrester’s installation location.

- Equipotential ring requirements for the surge arrester:

- At the 220 kV voltage level, it depends on the system and on the manufacturer’s technology.

- An additional equipotential ring may be installed at the top of the surge arrester to prevent corona discharge and to equalize the voltage distribution along the length of the arrester. The equipotential ring shall be made of metal or alloy capable of withstanding corrosion and rust caused by natural environmental conditions in substations, and shall have a structure suitable to create equipotential inside the sealed chamber of the surge arrester, thereby balancing the potential across the MO blocks.

      - Monitoring Components of the Surge Arrester (SA)

- The surge arrester shall be equipped with the following monitoring components:

- Discharge counter indicating the number of operations (number of discharge events through the SA). The counter shall have a minimum of 5 digits.

- Leakage current meter indicating the operating condition (showing the leakage current through the SA). The leakage current meter may include a feature for transmitting signals to remote monitoring equipment. The meter’s display panel may indicate the SA operating status levels such as: normal operation threshold, warning threshold, and out-of-service threshold.

- The discharge counter and the leakage current meter may be provided separately or integrated into one device. The manufacturer’s instruction manual must clearly specify whether the leakage current meter indicates the total leakage current or only the resistive component of the SA.

- Communication protocols and communication links between the monitoring system and the SAs shall be coordinated and standardized to ensure operational safety, so that overvoltage cannot propagate from the SAs to the substation control room.

      - Surge Arrester Base Insulation

- The surge arrester base insulation shall be made of porcelain or polymer, consistent with the arrester housing, for installation on the support structure. The base insulation shall withstand applied loads and ensure thermal, mechanical, and dielectric strength appropriate to the environmental conditions at the installation site.

      - Installation Arrangement

- The surge arresters shall be designed for direct installation on hot-dip galvanized steel supports. The steel used for the support structures shall have high strength and be capable of withstanding the loads of the surge arresters. The cross-sectional area of the support must be sufficiently large to meet the arrester manufacturer’s requirements, ensuring that during operation no excessive vibration of the arrester occurs which could affect its service life.

- Steel components (supports, beams, brackets, grounding parts, bolts, nuts, etc.) shall be hot-dip galvanized in accordance with TCVN 5408:2007, with a coating thickness not less than 80 µm, and shall comply with applicable standards for bolts and nuts.

- The grounding terminal of the surge arrester shall be marked with a “Earthing” symbol and positioned for convenient connection to the common grounding system of the substation. Grounding shall be carried out with insulated copper cable of cross-sectional area not less than 90 mm², with clamps suitable for proper connection.

- The leakage current meter and the discharge counter shall be installed in positions convenient for operation and maintenance, while considering and avoiding environmental impacts of the substation.

- Each surge arrester shall be provided with a nameplate and rating plate made of aluminum alloy, copper alloy, or stainless steel (Inox 304), showing all the main parameters of the arrester in accordance with manufacturing standards. The data on the rating plate and nameplate shall be durable, resistant to fading, and remain legible throughout the service life.

- High-voltage terminals and connecting leads of the surge arrester shall be selected and calculated in accordance with the arrester’s voltage rating, nominal discharge current, and terminal load capacity, ensuring safe and reliable operation.

- During installation, the manufacturer’s installation procedures for the surge arrester shall be strictly followed. Only accessories and materials of assured quality and approved by the manufacturer shall be used. The entire installation process must strictly comply with the manufacturer’s prescribed installation sequence.

      - Accessories

- The surge arrester shall be supplied complete with all necessary accessories for connection to phase/neutral conductors and the grounding system, as well as insulating mounting accessories for installation on metal support structures, and a lightning counter, including but not limited to:

- Suitable terminal clamps for connection to phase/neutral conductors and the grounding system.

- Grounding clamps and bolts compatible with copper conductors.

- Bolts, nuts, washers, and anti-loosening devices made of stainless steel or hot-dip galvanized steel.

- Surge arrester support structures and brackets (if any).

- Surge arrester mounting base.

- Accessories for connecting the lightning counter, insulating accessories for installation on metal support structures.

- Isolating switch (applicable in certain special cases in substations).

      - Other Requirements

- The equipment supplied shall be brand new, 100% unused, free from defects, accompanied by clear and legitimate Certificates of Origin (CO) and Certificates of Quality (CQ), together with supporting documents demonstrating compliance of the supplied goods with the design requirements and contractual provisions.

- The Bidding Documents or Equipment Procurement Contract shall include provisions requiring the Manufacturer to commit to warranty obligations in accordance with current commercial regulations as well as the requirements regarding the technical service life of the equipment.

      - Basic Technical Parameters of Surge Arresters

- The table of basic technical parameters of surge arresters: detailed in Technical Data Sheet

- Notes on selecting surge arrester parameters:

- Selection of insulation standard and creepage distance: 31 mm/kV

- Selection of rated parameters:

- Calculate the prospective short-circuit current of the area considering a 10-year outlook in order to select the appropriate rated short-circuit current.

- Perform insulation coordination calculations in the substation based on the results of transient overvoltage studies that may occur in the substation before and after installing the surge arrester, to ensure the selection of surge arrester is appropriate—providing the required protection for substation equipment while ensuring the safe operation of the surge arrester.

      - Requirements on Equipment Lifetime

- The reliability and lifetime requirements of the surge arrester (SA) shall be determined under the following minimum conditions:

- Number of discharge operations at rated discharge current without damage to the SA: at least 10 times.

- Service lifetime of the SA: at least 20 years.

      - Requirements on Surge Arrester Testing

- General requirements on surge arrester test documents:

- The manufacturer or supplier of surge arresters shall be responsible for providing complete test reports of surge arresters as specified in the Standards applied for surge arrester manufacturing.

- The technical specification shall stipulate the minimum tests that the manufacturer or supplier must provide prior to participating in equipment procurement bidding and prior to delivery to the purchaser.

- Requirements on surge arrester testing:

Requirements on surge arrester testing: For surge arresters, the applicable standards shall include: IEC 60099-4, IEEE C62.11, GB/T 1103,2…

- Type test:

The manufacturer shall provide documents demonstrating compliance with at least the following type tests in accordance with IEC 60099-4 standards:

- Insulation withstand tests on the arrester housing;

- Residual voltage test:

- Test to verify long term stability under continuous operating voltage

- Repetitive charge transfer withstand

- Heat dissipation behaviour verification of test sample

- Operating duty test:

- Power frequency voltage versus time

- Short circuit test;

- Bending moment;

For surge arresters with polymer insulating housings, the following additional tests are required to be provided:

- Weather ageing test

Type test reports shall be carried out by laboratories accredited in accordance with ISO/IEC 17025, or by the manufacturer’s own laboratories provided that the test results are witnessed by independent inspection bodies certified to ISO/IEC 17025, such as KEMA, CESI, ASTA, members of the STL association, etc.

- Routine test:

The factory test shall comply with the latest edition of IEC 60099-4 and as follows:

- Reference Voltage.

- Residual Voltage Test.

- Internal Partial Discharge Test.

- Power Frequency Voltage Test.

Routine test reports of the surge arrester shall be carried out and issued by the manufacturer itself.

Requirements on surge arrester testing: For surge arresters, the applicable standards shall include: ГОСТ Р 52725

- Type test:

The manufacturer shall provide documents demonstrating compliance with at least the following type tests in accordance with ГОСТ Р 52725 standards:

- Reference  voltage test (Классификационное напряжение)

- Residual voltage test (Остающееся напряжение при токе)

- Repetitive charge transfer withstand(Пропускная способность)

- Heat dissipation behaviour verification of test sample (Тепловая устойчивость)

- Insulation withstand test on the arrester housing (Электрическая прочность изоляции)

- Operating duty test (Характеристика «напряжение- время»)

- Mechanical test (Механическая прочность и Стойкость к вибрации)

Type test reports must be issued by laboratories accredited in accordance with ISO/IEC 17025 standards, or by the manufacturer’s laboratory; however, the test results must be witnessed by an independent inspection agency accredited with ISO/IEC 17025 certification

- Routine test:

The factory test shall comply with the latest edition of ГОСТ Р 52725 and as follows:

- Reference Voltage (Классификационное напряжение)

- Residual Voltage Test (Остающееся напряжение при токе)

- Internal Partial Discharge Test (Уровень частичных разрядов)

Routine test reports of the surge arrester shall be carried out and issued by the manufacturer itself.

All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements

      - Requirements on Surge Arrester Transportation

- Surge arresters shall be designed to allow easy disassembly, with each part packaged separately together with a packing list of materials for each package. They must be convenient for storage, transport (by machine or manual handling), and must allow for easy reinstallation and operation.

- Each surge arrester package shall be accompanied by a packing list of all items included. Measures shall be taken to prevent ingress of moisture, as well as the effects of seawater, thunderstorms, and other environmental factors.

      - Requirements for documents of Surge arrester

- The manufacturer shall be responsible for providing the following documents in full:

- Table of required surge arrester parameters.

- Drawings describing the structure, dimensions, and cross-sections of the main components of the surge arrester.

- Installation drawings (including drawings of equipment supports).

- Test reports in compliance with this Regulation and the applicable standards.

- Certificates of quality management system, product origin, and accessories.

- Manuals and recommendations covering: packaging, transportation, installation, operation, inspection, repair, equipment and accessory maintenance, periodic testing, type tests (including frequency and scope of work); common defects and failures; and troubleshooting methods.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

      - Other Requirements for Surge Arresters

- Items not specified in the “Basic Technical Specification of 220 kV Surge Arresters in Transmission Substations” shall comply with EVN and EVNNPT technical regulations, TCVN standards, and equivalent international standards.

      - Basic Data of 220kV Surge Arrester

Refer to Technical Data Sheet to have data of 220kV Surge Arrester

    - 110kV, 22kV Surge Arrester

#### General requirements

- 110kV and 22kV Surge Arresters according to the basic technical specification of transmission grid equipment, issued under Decision No. 110/QD-HDTV dated September 21, 2021 of EVN.

- To ensure lightning protection, surge arrester used for 110 kV, 22kV substations and distribution substations/switches that can protect both overvoltages due to lightning waves and overvoltages of operation, it is required to use a type of surge arrester gapless.

- SA has a shell made of porcelain or polymer, inside there are nonlinear MO reactors using ZnO type. MO has a small resistance value at overvoltage and a large value at rated operating voltage of the power system. If the shell is made of Polymer, the core must have a structure that ensures mechanical strength (such as fiberglass rods, load-bearing insulation bars, etc.) resistant to bending, twisting, resistant to fungus, not damaged by tear or impact, not cracked, sharp, degraded by environment and electric field.

- There is a self-relieve pressure in overload operating conditions for porcelain-shell Surge arresters.

- Environment conditions:

- Climatic condition			: Tropical

- Average air temperature		: 25°C

- Minimum air temperature		: 0°C

- Maximum air temperature		: 45°C

- Average humidity			: 85%

- Maximum humidity		: 100%

- Seismic factor 			: 0.015g

- Maximum wind speed		: 160km/h

- Creepage distance			:  31mm/kV

#### Installation Arrangement

- SA must be designed for direct mounting on steel supports.

- SA must be fully equipped with accessories for connection to the line/neutral line and grounding system, insulation kit for mounting on metal rack systems and lightning counters.

#### Requirements for testing

Routine Test:

The Routine Test for Surge Arrester shall comply with requirements according to IEC 60099-4, at least include the following items:

- Reference Voltage.

- Residual Voltage.

- Internal partial discharge test.

- Power- frequency voltage test.

Type Test:

The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

Type test must be performed by an ISO/IEC 17025 certified laboratory or manufacturer's laboratory but test results must be witnessed from independent international laboratory (with ISO certifications) like: KEMA, CESI, etc, including the following main items:

- Insulation withstand test on the arrester housing.

- Residual voltage

- Test to verify long term stability under continuous operation voltage.

- Repetitive charge transfer withstand.

- Heat dissipation behavior verification of test sample.

- Operation duty test.

- Power frequency voltage versus time - TOV.

- Short circuit test.

- Bending test.

- Polymer-housed surge arresters: Weather ageing test.

Note: All test have fully demonstrated the responsiveness of the equipment offered by bidders. The contractors may be rejected if does not meet the above requirements

#### Requirements for accessories

- Clamps for connection

- The bolt clamps used for grounding are copper wire compatible.

- The bolts and nuts respectively.

- Surge protection systems and supports (if any)

- Surge arrester mounting base.

- Surge counter.

#### Requirements for drawings and technical documents

The equipment shall be provided with the following drawings and technical documentation:

- The drawing depicts the general structure of the device.

- Installation instructions drawing.

- Documentation for installation, operation, repair and maintenance of equipment and accessories.

- The documents recommend inspection, maintenance, overhaul, how to handle common malfunctions.

- Test records and quality management

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016

#### Other requirement

- Equipment is 100% brand new, without defects, has a clear and legal certificate of origin (CO) and has a certificate of goods quality (CQ), together with relevant documents to prove it. Verify that the supplied goods conform to the design requirements and specified in the signed contract.

- Surge arrester must meet the durability for climatic and environmental conditions in Vietnam: tropicalized, suitable for operating environment conditions.

- Supports, beams, brackets, grounding, bolts, nuts and steel parts are hot-dip galvanized with coating thickness in compliance with Decision No. 428/QD-EVN dated 26/03/2025.

- Bolts manufactured according to TCVN 5571-1991, TCVN 1916-1995; nuts - washers according to TCVN 1905-76 standard.

- It is permissible to unpack and pack each part separately for shipping and a list of the number of supplies in each packing is required.

#### Basic Data of 110kV, 22kV Surge Arrester

- Refer to Technical Data Sheet to have data of 110kV, 22kV Surge Arrester.

      - CAPACITOR

110kV capacitors are selected according to Decision No. 111 / QD-HDTV dated September 21, 2021 and Decision No. 77 / QD-HDTV dated March 13, 2025 of the Electricity of Vietnam, Reactor to limiting discharge current are selected according to Decision No. 1859 / QD-EVNNPT dated 19/9/2025 of the Corporation. National electricity transmission.

- Appicable standards

[1] IEC 60071. Insulation co-ordination.

[2] IEC 60076-6:2007. Power transformers - Part 6: Reactors.

[3] IEC 60549:2013. High-voltage fuses for the external protection of shunt capacitors.

[4] IEC 60815. Selection and dimensioning of high-voltage insulators intended for use in polluted conditions

- IEC 60815-1:2008. Part 1: Definitions, .information and general principles.

- IEC 60815-2:2008. Part 2: Ceramic and glass insulators for a.c. systems.

- IEC 60815-3:2008. Part 3: Polymer insulators for a.c. systems.

[5] IEC 60871:2014. Shunt capacitors for a.c. power systems having a rated voltage above 1000 V.

- IEC 60871-1:2014. Part 1: General.

- IEC 60871-2:2014. Part 2: Endurance Testing.

- IEC 60871-3:2014. Part 3: Protection of shunt capacitors and shunt capacitor banks.

- IEC 60871-4:2014. Part 4: Internal fuses.

[6] IEC 61869. Instrument transformers.

- IEC 61869-1:2007. Part 1: General requirements.

- IEC 61869-2:2012. Part 2: Additional requirements for current transformers.

[7] IEC 62271. High-voltage switchgear and controlgear.

- IEC 62271-100:2017. Part 100: Alternating-current circuit-breakers.

- IEC 62271-102:2018. Part 102: Alternating current disconnectors and earthing switches.

- IEC 62271-108:2005. Part 108: High-voltage alternating current disconnecting circuit-breakers for rated voltages of 72,5 kV and above.

[8] IEC 60068-3-3:1991 Environmental testing - Part 3: Guidance. Seismic test methods for equipment.

[9] IEC 61000. Electromagnetic compatibility.

- IEC 61000-6-2:2016. Part 6-2: Generic standards - Immunity for industrial environments.

- IEC 61000-6-4:2018. Part 6-4: Generic standards - Emission standard for industrial environments.

[10] IEEE 18-2012. IEEE Standard for Shunt Power Capacitors.

[11] IEEE 1036-2010.IEEE Guide for Application of Shunt Power Capacitors.

[12] IEEE 693-2005. Recommended Practice for Seismic Design for Substations.

- Parameter requirements

- Parameters of capacitor unit: Refer to Technical datasheet

- Complex of 123kV capacitor bank: Refer to Technical datasheet

- Reactor to limiting discharge current: Refer to Technical datasheet

- Unbalance current transformer: Refer to Technical datasheet

- Technical requirements:

- Requirements on design, manufacture and installation

When designing and manufacturing the capacitor, the manufacturer must calculate and check the parameters of the capacitor to ensure that the equipment of the capacitor to be installed can withstand the working environment conditions., regional electrical system requirements, including and not limited to the following additional calculations:

- Power and rated current (Reactive Power and Current Rating);

- Working voltage capacitor meets the conditions stated in the request file;

- Transient voltage study;

- Research on the phenomenon of voltage recovery on the circuit breaker (Breaker transient recovery voltage study);

- Research on coordination to protect Spain (Relaying coordination study);

- Insulation coordination study;

- Calculation results for capacitor according to IEC 60871-1 requirements.

    - Requirements for Capacitor Unit

- General requirements

- Each capacitor unit is designed and manufactured from basic components including: 2 electrodes; insulating materials; protective cover of electrodes - insulating material; terminal ceramic chains for connecting component capacitors.

- Capacitor unit must be designed with materials to ensure minimum loss and maximize reliability. In capacitors it is forbidden to use environmentally hazardous substances such as PCBs. Do not use an external fuse to protect the capacitor.

- The rated voltage for capacitor unit is 15kV. This value can be changed to meet special design/manufacturing requirements for capacitor. The values ​​of lightning impulse withstand voltage and minimum leakage current for capacitors in the same phase and individual capacitors shall be selected by the Design Unit /Manufacturer and determined according to the design requirements /manufacture for capacitor and other insulation requirements.

- Capacitors can be interchanged within the capacitor unit in the same phase and between phases during installation and operation. Capacitor losses at rated voltage should not exceed 0.1 W/kVAr including losses related to dielectric, capacitor fuse, internal discharge resistance of capacitors, solder joints and conduction device in the capacitor.

- Capacitor tank is made from stainless steel or steel treated with powder coating. The surface treatment of the capacitor units shall ensure long-term stability, in the presence of both internal and external heating elements of the capacitor, as well as operation at the voltage specified in capacitor parameter request table.

- Test requirements for capacitor

When designing, manufacturing and testing the component capacitors must comply with the latest IEC 60871-1 and 60871-2 standards.

- Type test:

- Thermal stability test;

- Capacitor loss tangent (tan) measurement at elevated temperature;

- AC Voltage test between terminal and container;

- Overvoltage test;

- Lighting impulse voltage test between terminal and container;

- Short-circuit discharge test;

- Discharge test of internal fuses;

- Transient Overvoltage Test;

- Ageing test during 1000h at 1.4Un.

Type test items are required to have test records attached.

- Routine test:

- Capacitance measurement;

- Measurement of the tangent of the loss angle tanδ;

- Voltage test between terminals;

- AC voltage test between terminals and container;

- Test of internal discharge device;

- Sealing test.

- Discharge test of internal fuses.

It is the responsibility of the manufacturer to provide all records and results of the above tests.

- Information materials about capacitors

It is the responsibility of the manufacturer to provide, as a minimum, information about the component capacitors including:

- Capacitor capacitance including manufacturing tolerances;

- Rated voltage of the Component Capacitor Units;

- Insulation grade;

- Description of the internal protective fuse system, if any

- Weight and physical dimensions of the capacitors

- Capacitor configuration, including the number of parallel and series capacitors

- Type test and Routine Test records and results

The type test reports in accordance with the relevant testing standards must be performed and issued by the following laboratories:

- Internationally recognized testing laboratories which are members of STL (Short-Circuit Testing Liaison) organization; or

- The internationally recognized testing laboratories which are accredited according to the international standard ISO/IEC 17025:2017, with witnessed and issued by internationally recognized testing laboratories which are members of STL; or

- Internationally recognized testing laboratories accredited according to the international standard ISO/IEC 17025:2017 which are members of ILAC (International Laboratory Accreditation Cooperation).

- Additional regulations on condenser bracket installation materials

- Supporting structure hot dip galvanized (supporting structure according to manufacturer’s design). The Supporting structure are constructed so that any capacitor unit can be removed without disconnecting or removing other capacitors.

- These insulators must comply with IEC, IEEE standards as well as the Regulation on Insulators of EVNNPT.

    - Current limiting and discharge current reducing devices

- The purpose of the discharge current limiting and reducing device is to limit the influence of power frequency currents, as well as to provide the ability to reduce the oscillations caused by the discharge of the capacitors during operation switches Capacitor out of the busbar of the substation.

- The discharge current reducing device consists of a reactor with discharge current limiting, harmonic suppression and, in some cases, an additional damper resistor connected in parallel with the reactor. The reactor must be designed to be air core dry resistant. The damping resistors adopt dry resistor type and are connected continuously in parallel with the reactor.

- General requirements

- Discharge current limiting reactor must be single phase, air core design, self-cooling type and suitable for installation in outdoor environment conditions in substation construction area.

- The damping resistors must be single-phase, air-insulated, self-cooling and suitable for the installation of environmental conditions in the substation construction site.

- Reactor/Resistor must be able to withstand dynamic current that may appear when a fault occurs with discharge, overvoltage phenomena that may occur in the Capacitor.

- Discharge current limiting circuits must be designed for long-term operation in substations and capable of long-term operation with a voltage range not greater than the maximum design voltage required for the capacitor banks.

- The rated voltage of the reactor/resistor must meet the requirements of the Capacitor design. Rated values ​​and insulation level (BIL) are determined on the basis of technical design and calculation given.

- Test requirements for discharge current limiting reactor:

When designing, manufacturing and testing discharge current limiting reactors, the latest version of IEC 60076-6 must be complied with.

- Type test

- Short circuit current test;

- Temperature rise test.

- Routine test

- Measurement of winding resistance;

- Measurement of inductance;

- Measurement of loss and quality factor;

- Winding overvoltage test.

It is the responsibility of the manufacturer to provide all records and results of the above tests.

- Information materials on reactors limiting discharge current:

It is the responsibility of the manufacturer to provide, as a minimum, the following discharge current limiting reactors information:

- Inductance and resistance include manufacturing tolerances;

- Current, rated voltage and short-term withstand values;

- Insulation grade;

- Weight and physical dimensions of reactors;

- Type test and Routine Test records and results.

The type test reports in accordance with the relevant testing standards must be performed and issued by the following laboratories:

- Internationally recognized testing laboratories which are members of STL (Short-Circuit Testing Liaison) organization; or

- The internationally recognized testing laboratories which are accredited according to the international standard ISO/IEC 17025:2017, with witnessed and issued by internationally recognized testing laboratories which are members of STL; or

- Internationally recognized testing laboratories accredited according to the international standard ISO/IEC 17025:2017 which are members of ILAC (International Laboratory Accreditation Cooperation).

    - Unbalance current transformer:

- The neutral current transformers shall be used for measuring and protection purposes. They shall comply with IEC 61869-1; - 2.

- The neutral current transformer of capacitor is installed to determine the unbalanced current component in capacitor bay for the purpose of monitoring and determining the fault status of capacitor units in the capacitor bank.

- The main specifications applicable to the neutral current transformer: 5/1A-5P20-10VA.

- The secondary windings of the neutral current transformer must be connected to the protective relay for capacitor bay so that the protection and monitoring functions of the protective relay in capacitor bay work correctly.

      - POST INSULATOR

### General

- Post insulator according to the basic technical specification of transmission grid equipment, issued under Decision No. 103/QD-EVNNPT dated July 11, 2019 of EVNNPT

- Post insulator put into operation for power transmission grid is the type using single phase and outdoor. Post insulator was designed and manufactured by material such as porcelain and engineering which comply with Vietnamese standards, EVN/EVNNPT regulation and IEC standard and comply with Vietnamese weather condition.

- The support insulators required herein shall conform to the requirements of IEC 60071-1:2011, IEC 60071-2:2018, IEC 60168:2001, IEC 60273:1990, IEC 60437:1997, IEC 60507:2013, IEC 60660:1999, IEC 60815-1:2008, IEC 60815-3:2008, IEC 60815-3:2008.

### Basic physical characteristic of post insulator

- Voltage technical characteristic:

- Lightning impulse withstand voltage in dry condition.

- Switching impulse withstand voltage in dry/wet condition

- Power frequency withstand voltage in wet condition.

- Post insulator Puncture voltage.

- When we caculate the basic voltage for post insulator which will install on the future, and insulation co-ordinate with other equipments in substation we should use some standard below:

- IEC 60071 In the normal condition of working.

- IEC 60815 In the polution condition of working.

- Mechanical technical characteristic:

- Regulations about minimum failing load.

- Regulations about the dimension of post insulator, minimum nominal creepape distance

- Deflection when faced the bending strength

- Environment and other characteristic:

- Interference and anti-Interference of  Radio wave.

- Artificial polution

### Basic data for Post insulator

      - 220kV post insulator:

| Nominal system voltage | : 220kV |
| --- | --- |
| Rated voltage | : 245kV |
| IEC Designation | : IEC 60273 & IEC 60168 |
| Colour of glaze | : Chocolate brown |
| Materials | : Porcelain |
| Height | : > 2300 mm |
| Minimum creepage distance | : > 7595 mm |
| Lightning Impulse withstand voltage (1.2x50us) | : 1050 kV |
| Power frequency withstand voltage, wet | : 460 kV |
| Minimum failing load |  |
| Bending | : 10000 N |
| Torsion | : 4000 Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

      - 110kV Post Insulator:

| Nominal system voltage | : 110kV |
| --- | --- |
| Rated voltage | : 123kV |
| IEC Designation | : IEC 60273 & IEC 60168 |
| Colour of glaze | : Chocolate brown |
| Materials | : Porcelain |
| Height | : > 1220mm |
| Minimum creepage distance | : > 3813 mm |
| Lightning Impulse withstand voltage (1.2x50us) | : 550 kV |
| Power frequency withstand voltage, wet | : 230 kV |
| Minimum failing load |  |
| Bending | : 10000N |
| Torsion | : 4000Nm |

- The Post insulators shall be suitable for outdoor use and fitted with necessary clamp on the top of the insulator and provided with necessary mounting bolts, nuts and washers.

      - 22kV Post Insulator

| Nominal system voltage | 22kV |
| --- | --- |
| Rated voltage | 24kV |
| IEC Designation | IEC 60273 & IEC 60168 |
| Colour of glaze | Chocolate brown |
| Materials | Porcelain |
| Height | > 305mm |
| Minimum creepage distance | > 744 mm |
| Lightning Impulse withstand voltage (1.2x50us) | 125 kV |
| Power frequency withstand voltage, wet | 50 kV |
| Minimum failing load |  |
| Bending | 10.000N |
| Torsion | 1.200N-m |

### Minimum creepage distance

- Minimum creepage distance should caculate base on Vietnamese standards and belong to environment condition where we put the post insulator. In this project the Minimum creepage distance is 31mm/kV.

### Mechanical characteristic

      - Regulation about Falling load of Post insulator on the test for bending:

|  | Post insulator designation | Falling load |  |
| --- | --- | --- | --- |
|  |  | Load-bending (N) | Moment-torsion (Nm) |
| 220kV (C10-1050) | Class 10 | 10000 | 4000 |
| 110kV (C10-550) | Class 10 | 10000 | 4000 |
| 22kV (C10-125) | Class 10 | 10000 | 1200 |

      - Regulation about dimension of Post insulator:

- Porcelain post insulator with metal inside  should follow section 3 – Table 1 of IEC 60273

      - Regulation about surface of Post insulator:

- With post insulator use porcelain, we should use the post insulator which have equal enamel layer, equal colour, no cracked, no spot. The surface of post insulator should identical along the post insulator.

### Requirements for testing

- Test for post insulator shall comply with requiremens according to IEC 60168:2001 and should test report include post insulator.

- The type test, special test shall be performed and issued by the independent testing laboratories; or witnessed by the independent testing laboratories which are accredited according to the international standard ISO/IEC 17025:2005.

- Post insulator maintenance must follow the requirement, recommendation of manufacture as well as the regulations of operation unit.

      - Type Tests

- Type tests shall be made on all post insulators in accordance with the latest publication of IEC 60168.

- Copies of the type test report with certificate issued by accredited neutral testing laboratories which are accredited according to the international standard EN ISO/IEC 17025:2005. The certificate of Accreditation of the laboratory must be submitted as well.

- The required test are specified in IEC 60168:

Standard test:

- Dry lightning impulse withstand voltage test;

- Wet switching impulse withstand voltage test;

- Wet power frequency withstand voltage test;

- Mechanical failing load test.

Special test:

- Test for deflection under load;

- Radio interference test (IEC 60437);

- Artificial pollution test (IEC 60507).

      - Sample Test

- Sample tests shall be made on all post insulators in accordance with the latest publication of IEC 60168.

- Applicable on the number of post insulators selected at random from the lot:

- Verification of the dimensions;

- Temperature cycle test;

- Mechanical failing load test;

- Porosity test for ceramic insulators;

- Galvanizing test.

      - Routine Test

- Routine test shall be made on all post insulators in accordance with IEC 60168. Every post insulator shall be subjected to the applicable tests carried out in the following order:

- Routine visual inspection;

- Routine mechanical test (bending test), height > 770mm.

- Routine electrical test for post insulator in design categories 4 and 5 only (section 2.1.1 IEC 60168)

Note: All tests have to fully demonstrate the responsiveness of the equipment offer by bidder. The contractor may be rejected if does not meet the above requirement

### Requirements for transporting of post insulator

- Post insulator have to easily for removing, packing, transport by machine or handiwork and have easily allow for installing, operation.

- There is a table listing the number of equipment and material supplies in each package. Have solution to prevent moisture penetration and the impact of sea water.

### Requirements for documents of post insulator

- Manufacturer information, summary of post insulator specifications, origin of post insulator accessories, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, post insulator structural details drawings and accessories drawings.

- Instructions documents for installation, operation and maintenance of post insulator.

- Recommended documents when testing periodically: about frequency, content of work. Common defects and their handling. The drawings, sizes and code names for each type (or list of quantities - specifications).

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

### Other requirements for post insulator

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

### 220kV, 110kV, 22kV Post Insulator

- Refer to Technical Data Sheet to have data of 220kV, 110kV, 22kV Post Insulator

      - INSULATOR STRINGS

    - General requirements

- Technical standards for glass and ceramic insulators on EVNPT's transmission grid according to Decision No. 1769/QĐ-HĐTV dated September, 07,2025.

- String insulator put into operation for power transmission grid is the type using ceramic, glass. String insulator designed, made with material and technology which are checked, tested, supplied, transportation shall comply with TCVN, EVN and IEC.

- Insulator has snap cap shape, out-door and proper with tropical and temperate zone, fog, heavy duty, and lightning zone.

    - Codes and standards

- It is the intent of this specification to allow the supply of insulators according to IEC standard or other equivalent standards. The standards which shall be used in this Specification are listed below. Any standard proposed by the Bidder in place of or in addition to those specified shall be added.

BS 137    	Insulators of ceramic material or Toughened Glass for overhead lines with nominal greater than 1000V.

IEC 60305 (1995-12) 	Insulators for overhead lines with a nominal voltage above 1000 V - Toughened Glass or ceramic insulator units for a.c. systems - Characteristics of insulator units of the cap and pin type.

IEC 60383-1 	Insulators for overhead lines with a nominal voltage above 1000 V - Part 1: Toughened Glass or ceramic insulator units for a.c. systems - Definitions, test methods and acceptance criteria

IEC 60383-2  	Insulator strings and insulator sets for A.C. systems - Definitions, test methods and acceptance criteria.

IEC 60120 (1984-01) 	Dimensions of ball and socket couplings of string insulator units.

IEC/TR 60575 (1977-01) Thermal-mechanical performance test and mechanical performance test on string insulator units.

IEC/TR 60797 (1984-01) 	Residual strength of string insulator units of Toughened Glass or ceramic material for overhead lines after mechanical damage of the dielectric

IEC/TR 61211 Ed.2 (2004-11) Insulators of ceramic material or Toughened Glass for overhead lines with a nominal voltage greater than 1000V-Puncture testing

IEC 60815  Guide for the selection of insulators in respect of polluted conditions.

IEC/TR 61467 (Ed.1.0 2008-08) Insulators for overhead lines with a nominal voltage above 1000V-A.C power arc tests on insulator sets.

IEC 60437 Ed.2 (1997-09) 	Radio interference tests on high voltage insulators.

IEC 60060-1: High voltage test techniques – Part 1: General definitions and test requirements.

IEC 60507: 1991-04: Artificial pollution test on high voltage insulators to be used on A.C. systems.

IEC 60372: 1984-1 and Amendment No.1: 1991-09: Locking devices for ball and socket couplings of string insulator units – Dimensions and tests.

IEC 60071-1 Ed.8: 2011-03: Insulation co-ordination – Part 1: Definitions, principles and rules.

IEC 60071-2 Ed.8: 1996-12: Insulation co-ordination – Part 2: Application guide.

    - Requirements about structure and technical characteristic

- Insulator is string ball and socket type according to IEC 60305 and 60120, the upper part of insulator is cylinder, out door type, and proper with tropical and temperate zone, fog, heavy duty, and lightning zone.

- Cap and pin will not oxygenate, getting out of shape when they faced the mechanical load, making the change of distance of each insulator or rising the pressure on insulator.

- Cap make by cast iron or allumimum alloy and steel galvanized. Cap should round, in and outside part should concentric, no breaking, no roll up, no pock-marked, outside boundary will not rough to reducing electromagnetic concentration and making the interference of radio wave.

- Insulator make by glass or ceramic. The head of insulator where It will connect to pin should cylinder shape, this make the equal of pressure in insulator. Glass insulator have no fault as impurities, spume and the surface of insulator should identical.

- Pin make by forged steel and galvanized steel. Zinc sleeve on pin should follow IEC 61325 standard.

- The cement used to connect between cap and insulator as well as insulator and pin must be Aluminous, Portland cement that meets the requirements for inspection and testing of suspension insulators according to IEC 60305, IEC 60383, IEC and equivalent standards

- To avoid the slot between cap and glass insulator for reducing photo-electric, this slot must connect (can be insert by synthetic) and connect with electric paint, with the purpose when operation will not cause pock-marked  in this boundary and lead to photo-electric and interference.

- Cotter pin make by stainless steel, no ware out during the operation time.

- Galvanize and namplate must follow IEC 60380-1 standard,

- Insulator will be designed which are easily for checking, cleanning and fixing. Technical of insulator must stable during operation time on the power transmission grid. All equipment will be designed for making sure that they are always good on the environments condition where they put on and some case when occur the accident or the fault of system and short circuit.

- Electrical technical and mechanical follow the standard on the system line, the minimum creepage distance must follow Viet Nam standard (11TCN-19-2006, part II) and IEC 60815 standard.

    - Requirements for testing

#### Type test

- Type tests are intended to verify the basic characteristics of the insulation, which depend mainly on the engineering design. These tests are usually carried out on a small number of insulators and are carried out only once for a new design or new manufacturing process and then repeated only when there is a change in the design or manufacturing process. If the change affects only certain characteristics, it is only necessary to repeat the tests on those characteristics. In addition, electrical, mechanical and thermo-mechanical type tests need not be carried out on a new design of insulation if a valid test certificate is available for insulation of equivalent design and of the same manufacturing process.

- The type test according to IEC standards and equivalent standards, including the following:

i) Type test for insulators:

- Verification of the dimensions, according to IEC 60383-1 standard.

- Dry lighting impulse withstand voltage, according to IEC 60383-1 standard.

- Wet Power frequency withstand voltage, according to IEC 60383-1 standard.

- Electromechanical failling load test (for Porcelain Insulator), according to IEC 60383-1 standard.

- Mechanical failing load test (for Glass Insulator), according to IEC 60383-1 standard.

- Thermal-mechanical performance test, according to IEC 60383-1 standard.

- Residual strength test, according to IEC 60797 standard.

- Impulse voltage puncture test, according to IEC 61211 standard.

- Artificial pollution test, according to IEC 60507 standard.

ii) Type test for insulator sets: Type test for complete insulator set (including insulators and fittings fully assembled set), including the following:

- Corona test, according to IEC 61284 standard;

- Radio interference test, according to IEC 61284 and 60437 standard;

- Dry lighting impulse withstand voltage, according to IEC 60383-2 standard;

- Wet Power frequency withstand voltage, according to IEC 60383-2 standard;

- Power arc test, according to IEC 61467 standard;

- Mechanical failing load test, according to IEC 61284, IEC 61467  standard.

- Type tests must be performed at international independent laboratories. These laboratories must be certified to comply with ISO/IEC 17025 standard.

- In the case of test report is performed by the manufacturer, then this laboratory must meet: i) The manufacturer's laboratory must comply with ISO/IEC 17025; ii) The test results must be witnessed and confirmed by one of the international independent laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB (Canada), STL, JSTC, A2LA, UKAS or laboratories belonging to G8, Europe)

- The type test must cary on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025. (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

Note: All tests have to fully demonstrate the responsiveness of the equipment offer by bidder. The contractor may be rejected if does not meet the above requirement.

#### Rountine test

- This test is normal checking for complete products. Rountine test reports make by manufacture on each product which are made at the Factory to removing the fault unit. This type test reports shall comply with requiremens according to IEC 60383-1, include the tests below:

- Routine visual inspection.

- Rountine mechanical test.

- Rountine Electrical test.

- All this test must be confirm and take mark on each complete product.

#### Sample test, Factory acceptance test

        - Sample test for insulators

- Sample testing is carried out to check the properties that may vary during manufacture and the quality of the insulating material. Sample testing is used as an acceptance test on a random sample of insulators taken from a batch that has satisfied the relevant routine test requirements.

- Sample test is performed according to TCVN 7998-1:2009, IEC 60383 or equivalent standards.

- After passing the steps of routine testing, testing components (components) of insulation will test the following:

- Verification of the dimensions;

- Electromechanical failling load test (for Porcelain Insulator).

- Mechanical failing load test (for Glass Insulator).

- Measure the dimensions of the locking system;

- Temperature endurance test (for Porcelain insulators);

- Thermal shock test (for glass insulators)

- Insulation porosity and permeability test (for Porcelain insulators):

- Puncture withstand test;

- Galvanized Test;

- Check the displacement of the joints.

        - Sample test for insulator sets:

- For project with tender package for supplying materials and equipment, which is sets of insulator (including insulators + accessories fully assembled), in order to ensure the quality of equipment provided, the unit assigned to represent the investor is responsible for considering and deciding whether to test samples for set of insulator to ensure satisfy the requirements when it is put into operation. The sample test for set of insulator comply with TCVN, IEC or equivalent standards, including items:

- Dry lightning impulse withstand voltage test, according to IEC60383-2 standard.

- Wet power frequency withstand voltage test, according to IEC 60383-2 standard.

- Power arc test, according to IEC 61467 standard.

- Bidder is responsible for carrying out the sample test during the performance of the contract, when the goods are accepted for acceptance, the contractor must provide a sample test report that is correct with the product supplied for the project.

- The number of samples of insulator chains is selected for testing, the units in collaboration with Engineering of this project will propose at least 02 complete sets of insulator chains representing the shipment provided for the project, including 01 single/double suspention insulator set and 01 double/single tension insulator set.

- In case there is already a Type test (Type tets) for a set of accessory insulators that are correct for the product of the project, then it can be considered to accept without doing (post-test) Sample test (type test for insulator sets are correct for the product of the project: same insulator type, same fittings component, same manufacturer of insulators, fittings of insulator set offered).

- In case the Type tets for a set of accessory insulators are not consistent with the product supplied for the project, the sample test must be considered (post-test) in accordance with regulations.

- For cases of purchasing a small number of accessory insulator string sets for line repair, line connection, and transformer station connection with a variety of types and quantities of 200 string sets of each type or less, PMBs can consider accepting without having to perform a Sample test and the contractor must commit to ensuring the quality of the products included in the project.

- The sample test of insulator strings shall be performed at the independent testing laboratories (domestic or international) in accordance with ISO/IEC 17025 certificate, implement and issue test reports according to the above standards.

- Witnessing test confirmation by the buyer (if necessary) depending on each project is decided by the representative of the investor and agreed upon during contract negotiations.

- In the case of the type test performed by the manufacturer, then this lab must: i) the Lab of manufacturer must comply with ISO/IEC 17025, ii) Test results must be witnessed and confirmed by independent laboratories certified to ISO/IEC 17025.

- Notes: All type test have full demonstrated the responsiveness of the equipment offered by bidders. The Bidder will be rejected if does not meet the above requirements

#### Other technical requirement

- Insulator disc when use to install a complete string must be test, include the part according to IEC 60383-2, IEC 61467, IEC 60437 or equivalent.

- When carry out the equipment contract for project, insulator string contractor base on bidding technical requirements and caculate and supply detail caculation table of arcing horn distance for the contruction purposes.

#### Requiements for packing

- All packing use to pack the good must have clearly information: total weight, center of load… and heve the sign of regular vouchers.

- All of good must pack carefully then they can move by seaway, airway, railway, overland and make sure that the insulator is protected against bad weather conditions during the transport or storage.

- Each packing has a list with information about materials on the packing and the list will be put on the water-roof envelope. All good will register for easily checking purpose.

#### Requirements for transporting

- During transporting, the good must packed with each wood packing which are designed for damage preventting cause by clash. The good must be fasten by rope and avoid the shake down.

#### Requirements for Maintenance

- Insulator must pack on a wood packing or arrange on iron support and storage on a private store.

- When arrange insulator do not throw them.

- On the construction site, if do not install the insulator then they will keep on a store. Put them on wood packing or arrange each insulator together and put upper the floor 5-10cm.

#### Requirements for documents

- Manufacturer information, summary of insulator specifications, origin of insulator, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, structural details drawings and accessories drawings.

- Instructions documents for transortation installation, operation and maintenance of insulator.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

#### Other requirements

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

#### 220kV, 110kV String Insulator

- Refer to Technical Data Sheet to have data of 220kV, 110kV String Insulator.

      - FITTINGS

    - General requirements

- Technical specifications of fittings comply with the provisions of Decision No. 1769/QĐ-HĐTV dated September, 07,2025.

- Fittings are designed for outdoor use, suitable for operation in wet tropical climates, coastal areas, hoarfrost, industrial pollution areas, regions pollution caused by chemicals used in agriculture, snow-covered low temperature areas, areas with large thunderstorms.

- Fittings are designed, tested, manufactured and manufactured using materials and technologies that ensure to meet the standards and standards of Vietnam, the electricity industry, IEC and compliance. suitable for the climate of Vietnam.

    - Applicable codes and standards

[1] Decision 1769/QĐ-HĐTV dated September, 07,2025 of the National Power Transmission Corporation on promulgating regulations on basic technical characteristics of Fittings on electricity transmission grids

[2] IEC 61284 (1997-09): Overhead power lines - Overhead lines - Requirements and tests for Fittings.

[3] IEC 61854 (1998-09): Aerial power lines - Overhead lines - Requirements and tests for spacers.

[4] IEC 61897 (1998-09): Overhead lines - Requirements and tests for Overhead lines - Requirements and tests for Stockbridge type aeolian vibration dampers.

[5] IEC 60120 (1984-01): Dimensions of round ends and single junctions of single insulation.

[6] IEC 60372 (1984-01): Connection for single and round ends Amendment Nr.1 ​​(1991-09): Insulated chains - Dimensions and testing.

[7] IEC CISPR / TR 18-3 Ed.3.0en 2017: Radio interference properties of overhead lines and high-voltage equipment. Part 3: Technical process to minimize radio waves.

[8] BS 729: 1971: Hot-Dip Galvanized Coating on Ion & Steel Articles standard

[9] Decision No. 32/QĐ-HĐTV dated 04/02/2025 on the promulgation of the Operation and Maintenance Procedure for 220kV and 500kV Overhead Transmission Lines of the Members’ Council of EVNNPT.

[10] Decision No. 20 / QD-EVNNPT dated March 8, 2018 of the National Power Transmission Corporation on promulgating the Ministry of Procedures for operation and repair.

[11] IEC 60060-1: Kỹ thuật thử nghiệm điện cao áp, Phần 1: Định nghĩa chung và yêu cầu thử nghiệm (High Voltage test Techniques, Part 1: General definitions and test requirement).

[12] IEC 60437 Ed.2: 1997-09: Radio interference test on high voltage Insulators.

[13] IEC/TR 61467 Ed 1.0 2008-08: Insulators for overhead lines with nominal voltage above 1000V-AC. Power arc test on insulator sets.

[14] IEC 60071-1 Ed.8: 2011-03: Insulation co-ordination - Part1: definitions, principles and rules.

[15] IEC 60071-2 Ed.8: 1996-12: Insulation co-ordination - Part2: Application Guide.

    - Tension Clamp

      - Requirements about structure and technical

- Tension clamp put into operation is the type of outdoor and compression. Each tension clamp include: Aluminium tube for compression Aluminium conductor, Jumper terminal and bolt for tension clamp connecting.

- Aluminium tube for compression Aluminium conductor make by aluminium or aluminium alloy with good conductor of electricity, connect to conductor with bolt include screw and nut and tension clamp. Inside of tension clamp have available compound conductor of electricity and antirust and anticorrosive.

- Jumper terminal is monolithic member  include tension clamp and make by aluminium or aluminium alloy with good conductor of electricity, the title of jumper terminal between 0-30o. Jumper terminal make by M12, M14, M16 bolts depending on technical design requirements, depending on the wire type with corresponding conductor diameter/cross-section, the surface of Jumper terminal make sure that It good at conductor of electricity and contact. Inside of Jumper terminal have available compound conductor of electricity and antirust and anticorrosive.

- Tension Clamp must suitable with conductor, do not break conductor during the installation process, good at conductor of electricity, do not release Arc and can carry out the maximum short-circuit current according to calculation when when fault occurs.

- Breaking tension of tension clamp after compression not less than 90% minimum breaking tension of ACSR conductor. The resistance of tension clamp after compression is not more than 1,2 time of conductor.

- On each compartments of tension clamp must have product sign and main technical information. On each tube must carve inside some information like below:

- Name or logo of manufacture;

- Sign of tension clamp, Jumper terminal;

- Conductor type;

- Sign of Compression area;

- Marked the arrow and show the direction of compression;

- Each tension clamp must include the documents of dimension and detail technical information, Instruction manual of tension clamp and type of compression area.

      - Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent

#### Type test

- This test must follow IEC 61284 standard, at least include:

- Tension breaking test;

- Heating cycle test.

- Type tests must be performed at international independent laboratories. These laboratories must be certified to comply with ISO/IEC 17025 standard.

- In the case of test report is performed by the manufacturer, then this laboratory must meet: i) The manufacturer's laboratory must comply with ISO/IEC 17025; ii) The test results must be witnessed and confirmed by one of the international independent laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB (Canada), STL, JSTC, A2LA, UKAS or laboratories belonging to G8, Europe).

- The type test must carry on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025. (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

#### Rountine test

- When delivery good, The Contractor must give the Purchaser the rountine test. Rountine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Beside of these test, when the tension clamp install with the string insulator then the string insulate must suitable with the string insulator test.

    - Spacer Clamp

      - Requirements about structure and technical:

- This technical requirement is applied to the spacer clamp suitable for each type of AAC conductor with corresponding cross-section, installed on 220 kV, 110 kV lines with split-phase conductors 2-wire/1-phase. The distance between conductors in 1 phase will be specifically determined according to the technical design of each line.

- On the body of spacer clamp must have label. The lable required on the datasheet.

      - Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284, IEC 61854 standard or equivalent

      - Type test

- This test must follow IEC 61854, 61284 standard, at least include:

- Clamp slip test (IEC 61854);

- Torsional slip test (IEC 61854);

- Clamp bolt tightening test (IEC 61854);

- Corona voltage and RIV test (IEC 61284).

- The type test shall be performed and issued by the independent testing laboratories. The laboratories shall comply with ISO/IEC 17025.

- In the case of the type test performed by the manufacturer, then this lab must: (i) the Lab of manufacturer must comply with ISO/IEC 17025, (ii) The result must be witnessed and confirmed by the independent testing laboratories or witnessed by the independent testing laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB – Canada, STL, JSTC, A2LA, UKAS; or the LAB belong to G8, EUROPE).

- The type test must cary on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025 (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

      - Routine test

- When delivery good, The Contractor must give the buyer the routine test. Routine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284, IEC 61854, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Covering layer checking.

    - Suspension clamp

      - Requirements on structure and technical

- The suspension clamp is designed to synchronize with the insulator string to support the wire according to each type of wire as required.

- The suspension clamp is designed and manufactured with specifications to be suitable for each type of AAC-800, ACC-630  conductor, wire has the corresponding cross section.

- The suspension clamp should be light and have a structure that reduces vibration. The suspension clamp shall withstand the electromechanical destructive force equivalent to the corresponding supporting insulation sequence. The support lock is constructed as a joint to support the wire. Clamp body can rotate around one axis and this axis coincides with the center of the conductor.

- The Clamp body can rotate at least 45 degrees in the direction of up or down vertically. The suspension clamp should be made of a material that withstands the destructive load corresponding to the insulator string. The Contractor shall ensure that the calculations and designs are in accordance with the corresponding specific wire type and ensure that in operation, avoid resonance between the Clamp and the conductor or ground wire when being vibrated by the wind.

- Clamp body must be labeled on. The labeling is specified in the Technical specification offered.

      - Test and inspection

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent

#### Type test

- This test must follow IEC 61284 standard, at least include:

- Breaking load test.

- Slip test.

- Type tests must be performed at international independent laboratories. These laboratories must be certified to comply with ISO/IEC 17025 standard.

- In the case of test report is performed by the manufacturer, then this laboratory must meet: i) The manufacturer's laboratory must comply with ISO/IEC 17025; ii) The test results must be witnessed and confirmed by one of the international independent laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB (Canada), STL, JSTC, A2LA, UKAS or laboratories belonging to G8, Europe).

- The type test must carry on the product which are same manufacturer and country of manufacture.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025. (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing.

#### Rountine test

- When delivery good, The Contractor must give the Purchaser the rountine test. Rountine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284, and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- In addition to the above tests, when the suspension clamp is assembled synchronously with the insulator string, it is required to test the insulator string as prescribed.

    - Fittings of string insulator

      - Requirements about structure and technical:

- String insulator include some component like below:

- U bolt

- Ball eye

- Arcing horn

- Socket tongue

- U shackle

- Tension clamp

- Suspension clamp

- Insulator

…

- Technical requirements and testing of Tension clamp and Suspension clamp must follow item  Tension clamp and  Suspension clamp.

- Technical requirements and testing of Insulator must follow item Insulator Strings.

- All accessories of string insulator which are supply by contractor must design and make as the same thing on the drawings and requirements of bidding.

- Manufacture must supply calculate table of technical design, design drawings which show the technical requirements of bidding and must approve by the owner and designer.

- Spit pin should make by stainless steel.

- All accessories of string insulator must hot deep galvanized steel follow TCVN, ISO or BS 729 standard or equivalent.

- The surface of zinc coated must flat, clean, and uniform thickness and no fault.

- The arcing horn and arcing ring must design for string and conductor protecting when the electric discharge occur.

- The arcing horn designed to withstand high temperatures when short circuit currents occur. The arcing horn make sure that in the normal condition they have not arcing on the string and do not make the wave interference.

- On the body of spacer clamp must have label. The lable required on the datasheet.

      - Requirements for testing

- Requirements for testing, product acceptance must follow IEC 61284 standard or equivalent.

#### Type test

- This test must follow IEC 61284 standard, at least include breaking load test and requirements, test items according to Table 1 - IEC 61284 (Table 1- Tests on fittings).

- Type tests must be performed at international independent laboratories. These laboratories must be certified to comply with ISO/IEC 17025 standard.

- In the case of test report is performed by the manufacturer, then this laboratory must meet: i) The manufacturer's laboratory must comply with ISO/IEC 17025; ii) The test results must be witnessed and confirmed by one of the international independent laboratories (such as: KEMA, PEHLA, CESI, STLA, ASTA, SATS, ESEF, STLNA, POWER TECH LAB (Canada), STL, JSTC, A2LA, UKAS or laboratories belonging to G8, Europe).

- The type test must cary on the product which are same manufacturer, origin.

- Type test must include information below: (i) name, adress, sign/stamp of the lab, number of gain the standard certificate comply with ISO/IEC 17025. (ii) Testing product, part of test, applying standard, customer, date of testing, publish date of testing, Place of testing, detail of testing, method of testing, result of testing… (iii) Type, Manufacturer, origin of testing

#### Rountine test

- When delivery good, The Contractor must give the Purchaser the rountine test. Rountine test reports make by manufacture on each product which are made at the Factory to certificate the good is suitable with the technical information of contract. This type test reports shall comply with requiremens according to IEC 61284 and at least the tests below:

- Routine visual inspection.

- Dimention and marterial checking.

- Zinc coated checking.

- And requirements, test items according to table 1 - IEC 61284 (Table 1- Tests on fittings).

#### Sample test

- Sample test is performed according to IEC 61284 standard with requirements and items as table 1 - IEC 61284 (Table 1- Tests on fittings). The price is included in the bid price.

- Insulator set fittings sample test item including:

- Vissual exammination;

- Dimensional and material verification;

- Hot dip galvanizing;

- Mechanical tests - damage and failure load;

- Suspension clamps sample test:

- Vissual exammination;

- Dimensional and material verification;

- Hot dip galvanizing;

- Mechanical tests - damage and failure load;

- Slip test;

- Clamp bolt tightening test;

- Tension clamp sample test:

- Vissual exammination;

- Dimensional and material verification;

- Hot dip galvanizing;

- Mechanical tests - damage and failure load;

- Clamp bolt tightening test;

- Tensile test;

- Partial tension fittings sample test:

- Vissual exammination;

- Dimensional and material verification;

- Hot dip galvanizing;

- Insulator protective fittings sample test (arcing horn,…):

- Vissual exammination;

- Dimensional and material verification;

- Hot dip galvanizing;

      - Other requirements

- Galvanizing shall be performed in accordance with ISO standard or BS 729 or equivalent and apply for hot deep galvanizing process to gain the thickness not less than 610g/sp.m on the surface of steel pad... the coating thickness at saw-tooth will be 305g/sq.m

      - Requiements for packing

- All of good must pack carefully then they can move by seaway, airway, railway, overland and make sure that the insulator is protected against bad weather conditions during the transport or storage.

- All packing use to pack the good must have clearly information: total weight, center of load… and heve the sign of regular vouchers.

- Each packing has a list with information about materials on the packing and the list will be put on the water-roof envelope. All good will register for easily checking purpose.

- Informations on the packing list must include:

- Type, product sign;

- Total weight;

- Manufacture;

- Year of manufacture;

- Name of project, contruction;

- Hook Place

      - Requirements for transporting

- During transporting, the good must packed with each wood packing which are designed for damage preventting cause by clash. The good must be fasten by rope and avoid the shake down.

      - Requirements for Maintenance

- Insulator must pack on a wood packing or arrange on iron support and storage on a private store.

- On the construction site, if do not install the insulator then they will keep on a store. Put them on wood packing or arrange each insulator together and put upper the floor.

      - Requirements for documents

- Manufacturer information, summary of insulator specifications, origin of insulator, quality management certificate.

- There are all test records.

- Generally drawings with dimensions, sectional drawings, structural drawings, structural details drawings and accessories drawings.

- Instructions documents for installation, operation and warning on using.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

      - Other requirements

- The requirement are not mentioned in this document, it shall apply with IEC standard or equivalent.

      - TUBE, CONDUCTORS AND FITTINGS

    - General

The conductors and fittings supplied under this clause include:

- Aluminum tube: Ф160/144.

- Aluminum tube: Ф120/108.

- All Aluminium Conductor (AAC) 630sqmm.

- Aluminium Conductor steel reinforce (ACSR) 185/29sqmm.

- Fittings of Conductors

    - Requirements on structure and composition of materials

- Surface texture: The surface is uniform, the braids do not overlap, break or break as well as other defects that are harmful to the use process. At the ends and ends of the conductors, there must be cable caps or anti-twist belts.

- Twisted layers: The successive layers of helix must be opposite to each other and tightly twisted together, the outermost twisted layer in the right direction.

- Joints: During the braiding process, it is possible to connect broken aluminum wires, but the joints must comply with the provisions of IEC 61089. The joints must be welded by electric welding and then cold pressing. No joints are allowed on the wires of the steel core.

- The conductor (conductive part) consists of many small aluminum wires twisted around the core.

    - Requirements on origin and quality of raw materials

- Information regarding the origin of materials used for conductors must be clearly identified:

- Aluminum:

- Use aluminum ingots or use standard 9.5mm aluminum thread.

- Origin of imported aluminum (Manufacturer's name and address). Requirements for Suppliers of Aluminum Ingots to have a quality registered aluminum mark on the London Nonferrous Metals Exchange (LME registered).

- Before manufacturing, the manufacturer must present all legal documents proving the origin of imported materials.

- Aluminum ingot:

- Minimum aluminum content: 99.7%

- Maximum steel content : 0.2%

- Maximum Si content : 0.1%

- Other ingredients:

- Aluminum thread 9.5 mm .

- Minimum Conductivity : 61.3%

- Breaking stress : (70 -170) N/mm2

- Elongation : (2 -18)%

- Basic Data of conductor

- All Aluminium Conductor (AAC) 630sqmm: Refer to Technical Data Sheet to have data of Aluminium Conductor.

    - Test and inspection

- Conductor testing shall meet the requirements of IEC 61089, IEC 61395, TCVN 8090:2009 or equivalent standards.

- The tests must be conducted and issued or witnessed by an independent laboratory. These laboratories must be certified to comply with the prescribed standards.

- A type test record must be made on each type of conductor of the batch of products supplied under the contract and with the same manufacturer, country of manufacture.

- Type test report shall include the following information: (i) Name, address, signature/stamp of laboratory; (ii) Tested product, tested items, applied standards, client, date of test, date of publishing, test location, test details, test method, test result,…; (iii) Type, manufacturer, country of tested product.

#### Type test

- The type test record is made by an independent testing laboratory on each product similar to the product according to the design requirement of bidding documents to prove the suitable between required product and the designed product.

- Type test report: The Bidder must provide a Type test report for the conductor according to the bidding documents; The testing laboratory must be an independent and legally unit. Legally testing unit is a unit with testing function as prescribed and independent from organization, financially independent of manufacturers and suppliers.

- The Bidders are required to make a list of type test reports of the proposed equipment as required in clause 2.14. Required for list of type test reports.

- Test records must conform to IEC, TCVN or equivalent standards. The test covers the following main contents:

- Breaking strength of conductor according IEC 61089

- Stress-strain curves according IEC 61089

- Creep Test accoring  IEC 61395:1998

- Joints in aluminium wires accoring  IEC 61089;

#### Sample test

- Number of test samples in accordance with IEC 61089: Randomly select 2% of the total number of rolls for testing samples (in the case where the number of rolls is less than 100, take two samples).

- Time of sampling:

- For manufacturers: Before and after braided

- For acceptance of finished products: After braided

- Test contents: According to IEC 61089, TCVN 8090 or equivalent:

Testing before braided:

Aluminium/ Aluminium alloy wire:

- Appearance;

- Dimensions;

- Tensile test;

- Elongation test;

- Wrapping test;

- Conductivity test;

Hot-dip galvanised Zinc-coating steel wire:

- Appearance;

- Dimensions;

- Tensile test;

- Elongation test;

- Wrapping test;

- torsion test;

- mass of zinc

Testing after braided:

- Cross-section area;

- Overall diameter

- Linear density;

- Breaking strength;

- Surface condition;

- Lay ratio and direction of lay

- Mass of grease

- Before accepting delivery, it is necessary to witness testing and acceptance of products: the testing will be performed by an independent testing unit with legal status in the presence of the contractor, the purchaser and the agency. quality control (upon request).

- Addition to the above tests when checking and accepting products before delivery, manufacturers and suppliers must have a record of product inspection and testing to prove that the delivered products are in accordance with the specifications according to the specifications. requirements of the bidding documents. This record is made by an independent testing unit and conforms to IEC or TCVN standards, the contents of inspection and testing include the following:

- Check the number of aluminum fibers, the number of steel threads, the number of twist layers, the direction of the outer layer twist, the multiples of twist steps.

- Check aluminum fiber diameter, aluminum fiber bending, aluminum fiber relative elongation, aluminum fiber breaking stress.

- Check the steel wire diameter, the relative elongation of the steel wire, the 1% elongation stress of the steel thread, the tensile strength of the steel wire, the flexural strength of the steel thread, the coating of the steel thread.

- DC resistance of 1 km of conductor at 200C.

- Tensile force of the entire conductor.

- Wire weight.

- Elastic module.

- The coefficient of thermal expansion.

- Droplet temperature of grease.

    - Requirements Packaging and label

- Conductors (cables) will be placed in rollers with steel frames. Each type of cable will be wound on an independent roller. The outer diameter of the roller shaft must be large enough to avoid bending and damaging the conductor during winding or pulling.

- The frame of the roller must be sturdy enough to avoid damage to the conductors during transportation and handling. The conductor arm must have a cover plate and other ancillary parts to protect the cable during transportation as well as storage in the warehouse. Nails and other metal sharp objects used to close the spokes of the roller surface must not cause damage to the conductor.

- The ends of the conductors must be sealed with a seal or with a belt that does not allow the ends of the conductors to open. When winding conductors to the roller, the ends shall be fixed to the drum (conductor plate) of the roller. There is a cover that protects the outermost layer of the conductor arm, which cannot be removed until the conductor is installed.

- The conductor arm must be filled information  follow:

- The conductor arm must be filled with the following information

- Type and size of conductor

- Lead length (m)

- Total weight

- Number of lead wires

- Manufacturers Name

- Year of manufacture

- Project name and number

- Arrows determine the direction of rotation of the conductor

- The position of the hook to tie the load-bearing bridge

- Identification marks associated with appropriate transport documents

    - Requirements for transpostation

- When shipped, they must be packed in each finished roll and placed in the correct direction according to the manufacturer's instructions. Packages must be secured with ropes to avoid shaking and shifting during transportation.

    - Requirements for preservation

- Conductors are packed in rollers, stacked right on the load-bearing ground with self-spreading pads and stored in warehouses or covered yards.

- When loading and unloading, arrangements are not allowed to toss, roll, use cranes or forklifts and secure the ropes.

    - Requirments for document

- Information about the manufacturer, summary table of conductor parameters, origin, quality management certificate.

- A valid ISO quality control certificate from the conductor manufacturer is available upon request.

- Must have enough test records

- General drawings with dimensions, section drawings, structural drawings, detailed drawings of related structures of conductors

- Documentation for transportation, installation, operation and maintenance of conductors

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

    - Other requirements

- The requirement are not mentioned in this document, it shall apply with TCVN, IEC standard or equivalent.

      - HV TERMINAL CONNECTOR

    - General requirements

- Connectors and terminals for conductors shall be of bolted or compression type as stated in scope of supply, made of high grade aluminium alloy and fitted with bolts of hot-dip galvanized, and suitable for the various size conductors.

- Performances of clamps and connectors shall comply with the following standards: NEMA CC1, IEC 694.

- Connectors is manufacturered under Massive Anode technology, allow the connection suitable using for both cooper and aluminium alloy conductors without any semi-conductor sheets, tube or equipment designed not to cause corona and radio and audible noise in high-voltage installations up to 220kV.

- Where dissimilar metals are connected, approved means shall be provided to prevent eletcro technical action and corrosion.

- It has ability to carry the rated current that corresponding to the rated current of conductor is connected.

- It has ability to withstand the limited short circuit current:

- 50kA/1s at 220kV side

- 40kA/1s at 110kV side

- 25kA/1s at 22kV side

- The connector for aluminium conductor manufactures with enabling to reduce the corona effect, overheat effect. The surface of clamping plate has to abrade in oder to intensify contacting and treating to connect with other material, do not promote eletcro-chemical effect.

- The bolted plate processed by forged or casting method.

- Bolt and  screw of connector manufactured by hot dip galvanised, including packing ring and auto-lock when fully tightening force, it  guarantee to unloosen bolt by vibration. For connector used for conductor with diameter 400mm2 or above, at least 6 bolts will be applied.

- In the body of connector must be show information about devide code and other related information (if any).

- Connector that is submitted by bidder has enough information about ability to carry the rated current, withstand the limited short circuit current, voltage level.

    - Contact grease

- Contact grease is required and must be compound including metallic conductive particles which improve the electrical permanent contacts. The compound shall contain an inhibitor of corrosion. The grease protects the metal surfaces against the action of atmospheric oxygen and prevents the formation of oxides which increase the contact resistance.

- Electrical conductivity of contact grease must be less than electrical conductivity of connector.

    - Type Test

- Connectors must be tested by an internationally recognised independent testing laboratory which is accredited to the international standard EN ISO/IEC 17025:2005. The certificate of Accreditation of the laboratory must be submitted as well.

- The following type test reports shall be provided:

- Mechanical tensile test.

- Short circuit test.

- Temperature rise test.

- Slip strength of bolted type tension clamp test.

    - Document

- Outline drawings of HV terminal connector/clamp and accessories with dimensions and weights.

- Catalogue of HV terminal connectors/ clamps.

- Manual instructions for installation, operation, maintenance of HV terminal connectors/ clamps and accessories.

- And other requirements according to the content of dispatch No. 2152/EVNNPT-QLĐT-KT dated 02/06/2016.

      - SUPPORT STRUCTURES FOR EQUIPMENT

- Support structures shall be supplied together with all equipment under contract. The Supplier must design and manufacture the support structures in such dimensions that they match the foundations as per drawings of these Bidding Documents. Should for a good reason this not be possible, the Supplier has to inform the Purchaser hereof within latest three months after Contract Signing, indicating the reasons, and including an alternative proposal for the dimensions and arrangement of the fixing points for his structures.

- All support structures for electrical apparatus and equipment in the switchyard shall be galvanised H steel structures. They shall mount on the foundations as shown in the drawings section of these Bidding Documents.

- All steel parts must be hot-dip galvanized, quality according to 18TCN-02-92 or ASTM-123-89a or equivalent. The zinc coating shall be smooth, clean, of uniform thickness of at least 100µm (710 g/m²) and free from defects. The preparation for galvanizing and the galvanizing itself shall not adversely affect the mechanical properties of the coated material. All drilling, punching, cutting and bending of parts shall be completed and all burrs shall be removed before the galvanizing process is applied.

- Screw connections, bolts (quality according to TCVN 5571-1991); nuts, washers (quality according to TCVN 1096-76) etc. are also to be hot dip galvanizedin view of the high risk of corrosion, thickness min. 55µm (390g/m²) including the threaded portions. All nuts shall be galvanized with the exception of the threads, which shall be oiled.

- Materials on which galvanizing damage are detected after delivery to the construction site, shall be re-dipped unless, in the opinion of the Purchaser or his Representative, the damage is local and can be repaired by applying a coat of galvanizing repair paint. This repair paint must not adversely affect the final coating of the structure.

- Where additional coating is required, galvanized steel must be prepared by chemical treatment before coating. Galvanizing must be exposed to weathering for more than 6 (six) months prior to coating.

- The Contractor has to guarantee a life-time of the corrosion-protection of at least 30 (thirty) years (see also BS 5493/1977 Section 2).

- Surfaces shall be visually inspected. Bare patches, lumps, blisters or inclusions of foreign matter shall be cause for rejection.

- Zinc coating thickness shall be determined non-destructively by an appropriate instrument, however with thickness requirements as per the Contract Specification.

- The zinc coating of all galvanized structure components shall be inspected and tested in the manufacturer's works according to the following standards:

- For towers, bolts, screws, rivets: 18TCN - 02-92; DIN 50976, DIN 50978, DIN 50981, DIN 267 Part 10 and DIN 50982.

- Bolts: TCVN 5571-1991, DIN 50976, DIN 50978, DIN 50981, DIN 267 Part 10 and DIN 50982

- Nuts, Washers: TCVN 1096-76, DIN 50976, DIN 50978, DIN 50981, DIN 267 Part 10 and DIN 50982

- Thickness of coating shall be as per General Technical Specifications.

- The galvanizing tests are to be carried out as sample tests. The sampling rule is to be agreed with the Purchaser.

- Galvanizing Thickness:

- The galvanizing thickness shall be tested on site after receiving the galvanized components as well as during erection.  The zinc coatings must comply with the thickness requirements as specified.

- The Contractor shall make available on site for the Purchaser's use an instrument suitable for the accurate checking of galvanizing thickness. The measuring instrument shall be available from the time of arrival of the first consignment of steelwork until the issue of the taking over certificate.  The cost of the gauge and other operating expenses are deemed to be included in the Contract Price.

- Galvanizing Requirements:

- Except where specified to the contrary, all iron and steel used in the construction of the Contract Works shall be galvanized after sawing, shearing, drilling, punching, filling, bending and machining is completed.

- Galvanizing shall be performed in accordance with VDE Standard 0210 (see attachment) or BS 729.

- For galvanizing, only original blast furnace raw zinc shall be applied, which shall have a purity of 98.5%.

- The zinc coating shall be uniform, clean, smooth and as free from spangle as possible. Galvanizing shall be applied by the hot dip process and shall consist of a coating having at least the thickness shown in the table below:

---------------------------------------------------------------------------------------------------

Coating Thickness (Micrometer)

Components	                    No Significant	                    Medium Level

Pollution Areas	                    Pollution Areas

----------------------------------------------------------------------------------------------------

Steel Structures	                              100                                            100

Bolts, Screws, Nuts, Washers             55                                              55

----------------------------------------------------------------------------------------------------

- Steel structure materials shall be treated with Sodium Dichromate or Preton W20 solution after galvanizing to prevent the formation of white rust.

- Bolt, nuts, washers, locknuts and similar hardware shall be galvanized in accordance with the relevant standards. Excess spelter shall be removed by centrifugal spinning.

- Preparation for Galvanizing:

- All material to be galvanized shall be cleaned carefully of rust, loose scale, dirt, oil, grease, and other foreign substances. Particular care shall be taken to clean slag from welded areas.

- The preparation for galvanizing and the galvanizing itself shall not distort or adversely affect the mechanical properties of the material. After galvanizing, holes shall be free from nodules of spelter.

- Repair of Galvanizing:

- Material on which galvanizing has been damaged shall be re-dipped unless the damage is local and can be repaired by soldering or by applying a galvanizing repair compound, in this case, the compound shall be applied in accordance with the manufacturer's instructions.

- Soldering shall be done with a soldering iron using 50/50% solder (tin and lead). Surplus flux or acid shall be washed off promptly and the work shall be performed so as not to damage the adjacent coating or the metal itself. Any member on whom the galvanized coating becomes damaged after having been dipped twice shall be rejected.

- If any galvanized part is finally found to be imperfect, it shall be replaced. The whole of the expense involved in the replacement of the imperfect part shall be borne by the Contractor.

- The Contractor shall provide an instrument for checking galvanizing thickness, e.g. Elcometer, or otherwise agree with the Purchaser an approved method of testing galvanizing on Site.

- If, in the opinion of the Purchaser, the extent of damage found on site to a galvanized part appears capable of repair, the Contractor may, after receiving such agreement, attempt to effectively repair by approved methods. The agreement to attempt repair shall not bind the Purchaser to accept the repaired part when this is re-offered for inspection.

- In case it is found that galvanized parts are subject to the formation of white rust or damage resulting from chemical contamination, during shipment or storage on Site, the Purchaser shall either: Approve a system of scrubbing and protective painting to be applied on Site, if in his opinion expedient. Or forthwith order that the affected parts shall be condemned and that all future shipments shall receive, before dispatch from the Works, special dip or spray treatment to individual members to his approval without extra charge to the Purchaser.

- At least 3 holes for earthing are on support Structure.

      - DATA AND DOCUMENTATION REQUIREMENTS

    - General

- Supplier-furnished data and information shall be the guaranteed performance data, predicted performance, interface requirements and construction features of all Supplier’s furnished equipment. The accuracy of such information and its compatibility with overall performance requirements specified by Purchaser are the sole responsibility of the Supplier.

- All information submitted as part of Proposal Data will become part of contract data for successful bidder.

    - Data and Information to be submitted with the Bid

The following data shall be furnished together with the bid:

- Filled-in technical data of the Technical Data Sheets.

- Preliminary general assembly drawings indicating approximate overall dimensions, cable entrances, weights, nameplates, location of accessories, plans and section views, mounting and other details and clearances needed for operation and maintenance.

- Brochures and catalogues.

- Descriptive material, including construction and features of the equipment being proposed.

- Typical installation instructions.

- Reference list.

- Block diagram showing the proposed control scheme.

- Technical specification and description of equipment and device to be used.

- Control and instrumentation equipment layout.

- Brochure and supply experience of manufacturer in supplying relays.

- Photographs of similar relays of the type proposed by the Supplier.

- A written statement that for all equipment where type tests have been requested, these have been performed successfully and with it a summary of the type test reports.

- Shipping splits-approximate weight and size of major pieces.

- Supplier shall furnish a list of recommended spare or replacement parts as follows:

- Identification (Name of Part).

- Replacement time or parameters indicating the need to replace the above.

- Unit price of “1” above.

- Supplier shall specify the availability and location of spare parts permanently stocked by Supplier.

- Proposed time schedule to meet delivery date of  protection equipment.

- List of test equipment and special tools.

- Type test reports summary sheets for the equipment types (or similar type) included in the Bid.

- List of codes used.

- Tentative QA Program and ISO Certification.

- Bidders must provide a commitment to service life for each type of equipment offered in the bid.

- Bidder shall provide an (excellent) defect and failure rate for each type of equipment and commit to being on site to investigate and determine the cause of the defect, failure, or malfunction and to correct it. repair if due to technical errors of the manufacturer when requested by the investor.

Note:

- All documentaries submitted in the Bid must pursuant to requirement of bidding document;

- All documentaries aimed to prove the qualification and experience of bidder and manufacturer’s capacity, Manufacturer’s authorization letters, Test report, Certificates from realistic end-users for the similar or offered goods or other equivalent documents must be original version or certified regulated copy version.

- To Goods manufactured or processed from abroad, to be imported, the manufacturer has a reason for not being able to submit the original version or a certified true copy of type test report as prescribed when participating in the bid, the Bidder must provide in his bid a written statement from the Manufacturer confirming that the bid document is a photocopy of the original and the Manufacturer commits to be ready to work with the Purchaser to verify the document if is requested.

      - PACKING, SHIPPING AND TRANSPORT

- The Contractor shall be responsible for the packing, loading and transport of the plant from the place of manufacture, whether this is at its own works or those of any Supplier, to the destination, including off-loading.

- All apparatus shall be carefully packed for transport by sea, rail and road as necessary and ill such a manner that it is protected against climatic conditions.

- The method of packing shall provide adequate protection to the tank, and those parts contained within and attached without, for transportation.

- Precautions shall be taken to protect pans containing electrical insulation against the ingress of moisture.

- All bright parts liable to rust shall receive a coat of anti-rusting composition and shall be suitable protected. The machined face of all flanges shall be protected by means of a blank disc bolted to each face.

- Where appropriate all parts shall be boxed in substantial crates or containers to facilitate handling in a safe and secure manner. Each crate or container shall be marked clearly on the outside of the case to show where the mass is bearing and the correct position for the slings. Each crate or container shall also be marked with the notation of the part or pans contained therein, contract number and port of destination, and shall become the property of the Purchaser after delivery.

- Any damage due to defective or insufficient packing shall be made good by the Contractor at his own expense and within reasonable time when called upon by the Purchaser to do so. Five copies of complete packing lists showing tile number, size, marks, mass and contents of each package shall be posted to the Purchaser immediately the material is dispatched.

- The Contractor shall inform himself fully as to all relevant transport Facilities and requirements and loading gauges and ensure that the equipment as packed for transport shall conform to these limitations.

- The Contractor shall be responsible for all costs of repair or replacement of the equipment, including those incurred by the Purchaser, arising from damage during transport.

- There must be a list of the quantities of materials in each package for Circuit breakers (CBs), Disconnectors (DSs) offered. The shipping must be packaged separately for each CBs, DSs.

- Shipping is not allowed to disassemble and package separately for each Current Transformers (CTs), Capacitor Voltage Transformers (CVT).

- Measures should be taken to prevent the penetration of moisture and the effects of sea water for CBs, DSs, CTs, VTs, SAs.

      - REQUIRED FOR LIST OF TYPE TEST REPORT

- For each type of goods specified in the scope of supply and the detailed technical requirements for each type of goods, the Contractor is required to provide a statistic of the type test reports of the equipment as required in BD (attached with offered) is described in the following table:

LIST OF TYPE TEST REPORTS

| No. | Name of equipment | Manufacture/Country of Origin | Name of Laboratory | Name of Equipment | Name of Test | Dated of test/Nam of code | Standard | Evaluated | Remark |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 |
| 1 | Equipment |  |  |  |  |  |  |  |  |  |

- DATA SHEETS

The Data in the “Required” column of the following tables are to be read in conjunction with the descriptions in the technical specifications, and are requirements which the Supplier has to fulfill.

If there is any deviation from description of equipment and materials item of technical specifications, the data of this item (Data sheets) shall to be used.

The Bidder shall copy the following data sheets, completely fill in the "Tendered" column, and include them in his Bid. Each data sheet shall be initialled by the Bidder.

Where the space in the "Offered" Column is not sufficient to enter Bidder's information, a reference shall be made to separate sheets which are to be attached at the end of the section. Such additional sheets shall contain the specific information and data. References to general leaflets, catalogues etc. are not acceptable and may be evaluated as missing information.

# I. DATA SHEET FOR SUBSTATION

            - CIRCUIT BREAKERS

      - 220kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer Circuit Breaker |  |  |  |
| 1.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 1.2 | Designation |  | To be specified |  |
|  | Technical parammeters: |  |  |  |
| 2 | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
| 3 | Rated frequency | Hz | 50 |  |
| 4 | Method of neutral grounding |  | Directly earthed |  |
| 5 | Type |  | Outdoor, live tank, single-pole, SF6 insulated, single pressure (puffer) type |  |
|  | Voltage parammeters: |  |  |  |
| 6 | Nominal voltage | kV | 220 |  |
| 7 | Max. operation voltage of systems | kV | 242 |  |
| 8 | Rated voltage | kV | ≥245 |  |
| 9 | Rated short-duration power-frequency withstand voltage | kV |  |  |
| 9.1 | Phase-to-Earth | kV | ≥ 460 |  |
| 9.2 | Across the isolating distance | kV | ≥ 460 |  |
| 9.3 | Between phases | kV | ≥ 460 |  |
| 10 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) | kV peak |  |  |
| 10.1 | Phase-to-Earth | kV peak | ≥ 1050 |  |
| 10.2 | Across the isolating distance | kV peak | ≥ 1050 |  |
| 10.3 | Between phases | kV peak | ≥ 1050 |  |
| 11 | TRV peak values of transient recovery voltage |  |  |  |
| 11.1 | Terminal fault | kV | 364 |  |
| 11.2 | Short-line fault | kV | 280 |  |
| 11.3 | pha-Out-of-Phase | kV | 500 |  |
|  | Current parammeters: |  |  |  |
| 12 | Rated current | A | ≥ 2000 A (Hai Ha outgoing bay and transformer bay); ≥ 3150 A (bus coupler bay, tranfer bay and Huang Qiao outgoing bay) |  |
| 13 | Rated short-time withstand current | kA rms. | ≥ 50 |  |
| 14 | Rated duration of short-circuits | sec | ≥1 |  |
| 15 | Rated peak withstand current | kA peak | ≥ 125 |  |
| 16 | Rated line-charging breaking current | A rms | ≥ 125 |  |
| 17 | Rated cable-charging breaking current | A rms | ≥ 250 |  |
| 18 | Rated capacitive breaking curent | Arms | 400 |  |
| 19 | DC component of short-circuit breaking current | % | To be specified |  |
| 20 | Resistance of main contact (new contact) | µΩ | To be specified |  |
| 21 | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and electric) |  |
| 22 | Max. noise level due to operation of circuit breaker (IEC 62271-37-082) | dB | To be specified |  |
| 23 | On/Off Indicator |  | Yes |  |
| 24 | Circuit breaker performance: |  |  |  |
| 24.1 | Actuator of Circuit breaker |  | Single phase |  |
| 24.2 | Mechanical operation time without maintenance | Times | 10,000 cycles (closing-opening) |  |
| 24.3 | Number of operation at 100% rated current | Times | 2500 cycles (closing-opening) |  |
| 24.4 | Number of operation at 50% rated short circuit current | Times | 30 |  |
| 24.5 | Number of operation at 100% rated short circuit current | Times | 10 |  |
| 25 | Open/ close time: |  |  |  |
| 25.1 | open time | ms | ≤ 35 |  |
| 25.2 | close time | ms | To be specified |  |
| 25.3 | Total time for three pole discrepancy close or open | ms | ≤ 4 |  |
| 26 | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
| 27 | Minimum Clearance: |  |  |  |
| 27.1 | Between phases | mm | ≥ 2100 |  |
| 27.2 | Between phase and earth | mm | ≥ 2100 |  |
| 28 | Bushing insulator: |  |  |  |
| 28.1 | Applicable standard |  | According to IEC62155 or equivalent |  |
| 28.2 | Material |  | Brown porcelain |  |
| 28.3 | Minimum nominal creepage distance | mm/kV | 31 |  |
| 28.4 | Total creepage distance | mm | To be specified |  |
| 28.5 | Maximum impact load when Circuit breaker is in operation | kN | To be specified |  |
| 28.6 | Breaker terminal load capacity | kN | To be specified |  |
| 29 | Interrupting chamber systems, Circuit breaker poles: |  |  |  |
| 29.1 | There are desiccant, decomposition products and high pressure release device inside |  | Comply |  |
| 29.2 | Connection between poles or other parts by bolts |  | Comply |  |
| 30 | Interrupting chamber and arc extinguishing: |  |  |  |
| 30.1 | Arc extinguishing chamber structure |  | Stamping chamber not grounded (live tank) |  |
| 30.2 | Quantity of interrupting chamber per one pole |  | 01 |  |
| 30.3 | First-pole-to-clear factor | pu | 1.3 |  |
| - | Terminal fault | pu | 1.3 |  |
| - | Short-line fault | pu | 1 |  |
| - | Out-of-phase | pu | 2 |  |
| 30.4 | Insulating medium |  | SF6 |  |
| 31 | Number of closing coil |  | 1 coil/phase |  |
| 32 | Number of tripping coil |  | 2 coil/phase |  |
| 33 | Number of auxiliary contacts/1 phase |  |  |  |
| 33.1 | Normally open |  | 12 NO |  |
| 33.2 | Normally closed |  | 12 NC |  |
| 34 | SF6 gas system: |  |  |  |
| 34.1 | The meter indicates gas density |  | Temperature compensation type; 01 metter for 1 phases; Gas alarm circuit level 1, level 2. |  |
| 34.2 | Direct valve and Pressure relief device for SF6 gas |  | Yes |  |
| 34.3 | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
| 34.4 | Purity of SF6 | % | ≥ 98.5% V |  |
| 34.5 | Dew-point temperature | oC | Comply with IEC 60376 |  |
| 34.6 | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
| 34.7 | Rated SF6 density | kg/m3 | To be specified |  |
| 34.8 | First threshold of SF6 density | kg/m3 | To be specified |  |
| 34.9 | Second threshold of SF6 density | kg/m3 | To be specified |  |
| 35 | Local control cabinet: |  |  |  |
| 35.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 35.2 | Place of factory |  | To be specified |  |
| 35.3 | Designation |  | To be specified |  |
| 35.4 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) |  |
| 35.5 | Protection class |  | IP55 |  |
| 35.6 | Minimum thickness of cabinet cover | mm | ≥2 |  |
| 35.7 | Lock selection of local and remote control |  | Yes |  |
| 35.8 | Mechanism for opening/closing the circuit breaker |  | Yes |  |
| 35.9 | Counter |  | Yes |  |
| 35.10 | Other functional circuits depending on the type of circuit breaker (such as circuit breaker coil monitoring, power supply status, accumulator spring etc.) |  | Yes |  |
| 35.11 | Anti-pumping circuit |  | Yes |  |
| 35.12 | Out-of-phase protection circuit |  | Yes |  |
| 35.13 | There are overcurrent and overload protection circuits for the motor |  | Yes |  |
| 35.14 | Spring Charge Indicator |  | Yes |  |
| 35.15 | Heating system, lighting with LED lights, circuit-breakers |  | Yes |  |
| 35.16 | Energy storage structure |  | Energy spring (motor and crank) |  |
| 35.17 | Maximum spring charge time | s | 15 |  |
| 36 | Operating voltage: |  |  |  |
| 36.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 36.2 | Close coil | VDC | 220 (+10%; -25%) |  |
| 36.3 | Trip coil | VDC | 220 (+10%; -30%) |  |
| 36.4 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 36.5 | Maximum capacity of closing or tripping coils for all 3 phases | VA | 1200 |  |
| 37 | Steel supporting struture: |  | Manufacturer’s authorization letters |  |
| 37.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 37.2 | Material |  | Hot dip galvanized |  |
| 38 | HV terminal connector |  |  |  |
| 38.1 | Manufacturer/ Country of Origin |  | To be specified |  |
| 38.2 | Materials |  | Aluminum alloy |  |
| 38.3 | Dimensions |  | Suitable for designed conductor |  |
| 39 | Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker according to 2878/EVNNPT-KT ngày 17/08/2018 doccument |  | Required |  |
| 40 | Type test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 41 | Technical documents |  | English/Vietnamese |  |
| 42 | Catalogues |  | To be supplied |  |
| 43 | The remaining parameters or different will comply with the provisions of 272/QĐ-EVN and 1677/QĐ-EVNNPT dated 24/08/2025 and 2416/QĐ-EVNNPT dated 09/12/2025 |  | Yes |  |

      - 110kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer Circuit Breaker |  |  |  |
| 1.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 1.2 | Designation |  | To be specified |  |
|  | Technical parammeters: |  |  |  |
| 2 | Applicable standard |  | IEC 62271-100, IEC 62271-1 |  |
| 3 | Rated frequency | Hz | 50 |  |
| 4 | Method of neutral grounding |  | Directly earthed |  |
| 5 | Type |  | Outdoor, live tank, 3 phase, SF6 insulated, pressure (puffer) type |  |
|  | Voltage parammeters: |  |  |  |
| 6 | Nominal voltage | kV | 110 |  |
| 7 | Max. operation voltage of systems | kV | 121 |  |
| 8 | Rated voltage | kV | ≥123 |  |
| 9 | Rated short-duration power-frequency withstand voltage | kV |  |  |
| 9.1 | Phase-to-Earth | kV | ≥ 230 |  |
| 9.2 | Across the isolating distance | kV | ≥ 230 |  |
| 9.3 | Between phases | kV | ≥ 230 |  |
| 10 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) | kV peak |  |  |
| 10.1 | Phase-to-Earth | kV peak | ≥ 550 |  |
| 10.2 | Across the isolating distance | kV peak | ≥ 550 |  |
| 10.3 | Between phases | kV peak | ≥ 550 |  |
| 11 | TRV peak values of transient recovery voltage |  |  |  |
| 11.1 | Terminal fault | kV | 183 |  |
| 11.2 | Short-line fault | kV | 141 |  |
| 11.3 | pha-Out-of-Phase | kV | 251 |  |
|  | Current parammeters: |  |  |  |
| 12 | Rated current |  | ≥ 2000 A (Coupler bay, tranfer bay and transformer bay); ≥ 1250 A (outgoing bay) |  |
| 13 | Rated short-time withstand current | kA rms. | ≥ 40 |  |
| 14 | Rated duration of short-circuits | sec | ≥ 1 |  |
| 15 | Rated peak withstand current | kA peak | ≥ 100 |  |
| 16 | Rated line-charging breaking current | A rms | ≥ 31,5 |  |
| 17 | Rated cable-charging breaking current | A rms | ≥ 140 |  |
| 18 | Rated capacitive breaking curent | Arms | 400 |  |
| 19 | DC component of short-circuit breaking current | % | To be specified |  |
| 20 | Resistance of main contact (new contact) | µΩ | To be specified |  |
| 21 | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and electric) |  |
| 22 | Max. noise level due to operation of circuit breaker (IEC 62271-37-082) | dB | To be specified |  |
| 23 | On/Off Indicator |  | Yes |  |
| 24 | Circuit breaker performance: |  |  |  |
| 24.1 | Actuator of Circuit breaker |  | 3 phase |  |
| 24.2 | Mechanical operation time without maintenance | Times | 10,000 cycles (closing-opening) |  |
| 24.3 | Number of operation at 100% rated current | Times | 2500 cycles (closing-opening) |  |
| 24.4 | Number of operation at 50% rated short circuit current | Times | 30 |  |
| 24.5 | Number of operation at 100% rated short circuit current | Times | 10 |  |
| 25 | Open/ close time: |  |  |  |
| 25.1 | open time | ms | ≤ 35 |  |
| 25.2 | close time | ms | To be specified |  |
| 25.3 | Total time for three pole discrepancy close or open | ms | ≤ 4 |  |
| 26 | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
| 27 | Minimum Clearance: |  |  |  |
| 27.1 | Between phases | mm | ≥ 1100 |  |
| 27.2 | Between phase and earth | mm | ≥ 1100 |  |
| 28 | Bushing insulator: |  |  |  |
| 28.1 | Applicable standard |  | According to IEC62155 or equivalent |  |
| 28.2 | Material |  | Brown porcelain |  |
| 28.3 | Minimum nominal creepage distance | mm/kV | 31 |  |
| 28.4 | Total creepage distance | mm | To be specified |  |
| 28.5 | Maximum impact load when Circuit breaker is in operation | kN | To be specified |  |
| 28.6 | Breaker terminal load capacity | kN | To be specified |  |
| 29 | Interrupting chamber systems, Circuit breaker poles: |  |  |  |
| 29.1 | There are desiccant, decomposition products and high pressure release device inside |  | Comply |  |
| 29.2 | Connection between poles or other parts by bolts |  | Comply |  |
| 30 | Interrupting chamber and arc extinguishing: |  |  |  |
| 30.1 | Arc extinguishing chamber structure |  | Stamping chamber not grounded (live tank) |  |
| 30.2 | Quantity of interrupting chamber per one pole |  | 1 |  |
| 30.3 | First-pole-to-clear factor | pu | 1.5 |  |
| - | Terminal fault | pu | 1.3 |  |
| - | Short-line fault | pu | 1 |  |
| - | Out-of-phase | pu | 2 |  |
| 30.4 | Insulating medium |  | SF6 |  |
| 31 | Number of closing coil |  | 1 coil/phase |  |
| 32 | Number of tripping coil |  | 2 coil/phase |  |
| 33 | Number of auxiliary contacts/1 phase |  |  |  |
| 33.1 | Normally open |  | 12 NO |  |
| 33.2 | Normally closed |  | 12 NC |  |
| 34 | SF6 gas system: |  |  |  |
| 34.1 | The meter indicates gas density |  | Temperature compensation type; 01 metter for 3 phases; Gas alarm circuit level 1, level 2. |  |
| 34.2 | Direct valve and Pressure relief device for SF6 gas |  | Yes |  |
| 34.3 | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
| 34.4 | Purity of SF6 | % | ≥ 98.5% V |  |
| 34.5 | Dew-point temperature | oC | Comply with IEC 60376 |  |
| 34.6 | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
| 34.7 | Rated SF6 density | kg/m3 | To be specified |  |
| 34.8 | First threshold of SF6 density | kg/m3 | To be specified |  |
| 34.9 | Second threshold of SF6 density | kg/m3 | To be specified |  |
| 35 | Local control cabinet: |  |  |  |
| 35.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 35.2 | Place of factory |  | To be specified |  |
| 35.3 | Designation |  | To be specified |  |
| 35.4 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) |  |
| 35.5 | Protection class |  | IP55 |  |
| 35.6 | Minimum thickness of cabinet cover | mm | ≥2 |  |
| 35.7 | Lock selection of local and remote control |  | Yes |  |
| 35.8 | Mechanism for opening/closing the circuit breaker |  | Yes |  |
| 35.9 | Counter |  | Yes |  |
| 35.10 | Other functional circuits depending on the type of circuit breaker (such as circuit breaker coil monitoring, power supply status, accumulator spring etc.) |  | Yes |  |
| 35.11 | Anti-pumping circuit |  | Yes |  |
| 35.12 | Out-of-phase protection circuit |  | Yes |  |
| 35.13 | There are overcurrent and overload protection circuits for the motor |  | Yes |  |
| 35.14 | Spring Charge Indicator |  | Yes |  |
| 35.15 | Heating system, lighting with LED lights, circuit-breakers |  | Yes |  |
| 35.16 | Energy storage structure |  | Energy spring (motor and crank) |  |
| 35.17 | Maximum spring charge time | s | 15 |  |
| 36 | Operating voltage: |  |  |  |
| 36.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 36.2 | Close coil | VDC | 220 (+10%; -15%) |  |
| 36.3 | Trip coil | VDC | 220 (+10%; -30%) |  |
| 36.4 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
| 36.5 | Maximum capacity of closing or tripping coils for all 3 phases | VA | 1200 |  |
| 37 | Steel supporting struture: |  | Manufacturer’s authorization letters |  |
| 37.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 37.2 | Material |  | Hot dip galvanized |  |
| 38 | HV terminal connector |  |  |  |
| 38.1 | Manufacturer/ Country of Origin |  | To be specified |  |
| 38.2 | Materials |  | To be specified |  |
| 38.3 | Dimensions |  | Suitable for designed conductor |  |
| 39 | Installation supervision, Supervision of Testing and Commissioning for Circuit Breaker according to 2878/EVNNPT-KT ngày 17/08/2018 doccument |  | Required |  |
| 40 | Type test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 41 | Technical documents |  | English/Vietnamese |  |
| 42 | Catalogues |  | To be supplied |  |
| 43 | The remaining parameters or different will comply with the provisions of 272/QĐ-EVN and 1677/QĐ-EVNNPT date 24/08/2025 |  | Yes |  |

      - 22kV Circuit Breaker

| Item No | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-100 |  |
|  | Type |  | Outdoor, live tank, three poles, SF6 or Vacuum insulated, single pressure (puffer) type |  |
|  | Insulating medium |  | SF6 or Vacuum |  |
|  | Stamping chamber structure |  | Live tank |  |
|  | Number Stamping chamber/1 phase |  | 01 |  |
|  | Nominal voltage | kV | 22 |  |
|  | Rated voltage | kV | ≥ 24 |  |
|  | Rated current | A | ≥ 630 |  |
|  | Frequency | Hz | 50 |  |
|  | Rated three phase symmetrical short-circuit breaking current | kA rms. | ≥ 25 |  |
|  | Rated peak withstand current | kA peak | ≥ 62.5 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Rated Operating Sequence |  | O-0.3sec.-CO -3min -CO |  |
|  | Lightning impulse voltage (1.2/50µs) withstand - Between Phase - earth - Between Phase - Phase - Across the isolating distance | kV peak | ≥ 125 |  |
|  | One minute power frequency voltage withstand 50 Hz - Between Phase - earth - Between Phase - Phase - Across the isolating distance | kV rms. | ≥ 50 |  |
|  | First-pole-to-clear factor | pu | 1.5 (IEC 62271-100) |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Chamber system, pole center of CB |  | - There are dehumidifiers, decomposition products and high pressure release parts inside; - Links between the pole or other parts with bolts; |  |
|  | Bushing insulator: |  |  |  |
| 21.1 | Applicable standard |  | According to IEC 62155 or equivalent |  |
| 21.2 | Material |  | Brown porcelain |  |
| 21.3 | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| 21.4 | Total minimum nominal specific creepage distance | mm | To be specified |  |
| 21.5 | Maximum impact load when the circuit breaker is in operation | kN | To be specified |  |
| 21.6 | Circuit Breaker terminal load capacity | kN | To be specified |  |
|  | Mechanical operation duration |  | ≥ 10,000 cycles (closing-opening). |  |
|  | Operation with rate current duration |  | ≥ 2,500 cycles (closing-opening) |  |
|  | Total trip time with 3 phases short-circuit (not overhaul) |  | ≥ 20 cycles |  |
|  | Operating mechanism drive type |  | Spring (There is a charge indicator, both manual and electric) |  |
|  | Protection class of drive cabinet, Local control cabinet |  | IP55 |  |
|  | Openning time | ms | ≤60 |  |
|  | Closing time | ms | ≤ 80 |  |
|  | Number of spare auxiliary contacts (Repeating aux. switch contact via aux. contactor or aux. relay shall be not accepted) |  |  |  |
| 29.1 | Normally open |  | ≥ 6 |  |
| 29.2 | Normally closed |  | ≥ 6 |  |
|  | Number of closing coil |  | 1 coil/phase |  |
|  | Number of tripping coil |  | ≥ 1 coil |  |
|  | SF6 gas |  | (Applies to SF6 Circuit Breaker) |  |
| 32.1 | The meter indicates gas density |  | - Temperature compensation type - 01 metter for 3 phases. - Gas alarm circuit level 1, level 2 (alarm, lock). |  |
| 32.2 | Pressure relief device for SF6 gas |  | Yes |  |
| 32.3 | Leakage of SF6 per year | %/year | ≤ 0.5 |  |
| 32.4 | Purity of SF6 | % | ≥ 98,5% V |  |
| 32.5 | Dew-point temperature | oC | Comply with IEC 60376 |  |
| 32.6 | SF6 mass for one three-pole circuit breaker | kg | To be specified |  |
| 32.7 | Rated SF6 density | kg/m3 | To be specified |  |
| 32.8 | First threshold of SF6 density | kg/m3 | To be specified |  |
| 32.9 | Second threshold of SF6 density | kg/m3 | To be specified |  |
|  | Local control cabinet |  |  |  |
| 33.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 33.2 | Place of factory |  | To be specified |  |
| 33.3 | Designation |  | To be specified |  |
| 33.4 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) |  |
| 33.5 | Protection class |  | IP55 (According to IEC 60529) |  |
| 33.6 | Circuit breaker parameter table name plate |  | Made of stainless material, the lettering does not fade during the life of the circuit breaker |  |
| 33.7 | Anti-pumping circuit |  | Yes |  |
| 33.8 | Other fuctions circuit (trip coil supervision circuit, power state of ATM circuit, uncharged springs circuit…) |  | Yes |  |
| 33.9 | Full device and accesories for operational in “local” and “remote” mode |  | Yes |  |
| 33.10 | Mechanical opening / closing operations |  | Yes |  |
| 33.11 | MCB for power-supply of drying and lighting has separate contact. |  | Yes |  |
| 33.12 | Operating counter |  | Yes |  |
| 33.13 | Overcurrent and overload protection circuit for the motor |  | Yes |  |
| 33.14 | Spring charge indicator |  | Yes |  |
| 33.15 | Other auxiliary equipment |  | Full set according to the manufacturer's design |  |
|  | Auxiliary supply voltage: |  |  |  |
| 34.1 | Motor | VDC | 220 (+10%; -15%) |  |
| 34.2 | Close coil | VDC | 220 (+10%; -15%) |  |
| 34.3 | Trip coil | VDC | 220 (+10%; -30%) |  |
| 34.4 | Heating and Lighting | VAC | 220 (+10%; -15%) |  |
|  | Steel supporting struture |  | Manufacturer’s authorization letters |  |
| 35.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 35.2 | Material |  | Hot dip galvanized |  |
|  | Accessories |  |  |  |
| 36.1 | HV terminal connector: |  |  |  |
| - | Materials |  | Aluminum alloy |  |
| - | Dimensions |  | Suitable for designed conductor |  |
| - | Number of holes (Min 6 holes) |  | To be specified |  |
| - | Size of holes, spacing of holes |  | To be specified |  |
| 36.2 | Manual spring accumulator |  | Yes |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | Technical document |  | English/Vietnamese |  |

- DISCONNECTOR AND EARTHING SWWITCH

  - 220kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacturer/ Country of Origin |  | To be specified |  |
| 2 | Designation |  | To be specified |  |
| 3 | Technical parammeters: |  |  |  |
| 3.1 | Applicable standard |  | IEC 62271-102 |  |
| 3.2 | Rated frequency | Hz | 50 |  |
| 3.3 | Method of neutral grounding |  | Directly earthed |  |
| 3.4 | Type |  | Outdoor |  |
| 3.5 | Configuration of one set |  | 1 phase/3 phase |  |
| 3.6 | Blade opening type |  | horizontal rotary |  |
| 3.7 | Number of earthing switches for the disconnector |  | 0 ES/ 1 ES/ 2 ES |  |
| 4 | Voltage parammeters of disconnector: |  |  |  |
| 4.1 | Nominal voltage | kV | 220 |  |
| 4.2 | Max. operation voltage of systems | kV | 242 |  |
| 4.3 | Rated voltage | kV | 245 |  |
| 4.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 460 530 |  |
| 4.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 1050 1200 |  |
| 5 | Current parammeters: |  |  |  |
| 5.1 | Rated current | A | ≥ 2000 A (Hai Ha outgoing bay and transformer bay); ≥ 3150 A (bus coupler bay, tranfer bay and Huang Qiao outgoing bay) |  |
| 5.2 | Rated short-time withstand current | kA | ≥ 50 |  |
| 5.3 | Rated duration of short-circuit | s | ≥ 1 |  |
| 5.4 | Rated peak withstand current | kA | ≥ 125 |  |
| 5.5 | Resistance of main contact (new contact) | µΩ | To be specified |  |
| 6 | Technical parammeter of earthing switch: |  |  |  |
| 6.1 | Rated short-circuit making current | kA | 50 |  |
| 6.2 | Rated induced current of electrostatic coupling | Arms | 3 |  |
| 6.3 | Rated induced current of electromagnectic coupling | Arms | 80 |  |
| 6.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥ 283 |  |
| 7 | Operational capacity of disconnector and earthing switch: |  |  |  |
| 7.1 | Disconnector drive |  | Single phase/ three phase |  |
| 7.2 | Mechanical endurance class |  |  |  |
| - | Disconnector |  | M1 |  |
| - | Earthing switch |  | M0 |  |
| 7.3 | Total mechanical switching times, without maintenance |  |  |  |
| - | Disconnector | Times | ≥ 2000 |  |
| - | Earthing switch | Times | ≥ 1000 |  |
| 7.4 | Operation Tools for open/close DS and ES |  | Yes |  |
| 7.5 | Mechanical interlock between DS and ES |  | Yes |  |
| 7.6 | Total weight of 3-pole unit | kg | To be specified |  |
| 8 | Clearance: |  |  |  |
| 8.1 | Between phase and earth | mm | ≥ 2100 |  |
| 8.2 | Between two poles/phase | mm | ≥ 2100 |  |
| 9 | Support Insulator: |  |  |  |
| 9.1 | Applicable standard |  | According to IEC 60273 or equivalent |  |
| 9.2 | Material |  | Brown porcelain |  |
| 9.3 | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| 9.4 | Total minimum nominal specific creepage distance | mm | To be specified |  |
| 9.5 | Mechanical terminal load - For three phases disconnector and earthing switch: + Straight load Fa1, Fa2 + Cross load Fb1, Fb2 - For single phase disconnector and earthing switch: + Straight load Fa1, Fa2 + Cross load Fb1, Fb2 Vertical Force, Fc | kN | 0.8: Ir≤2500A 1.0: Ir>2500A 0.27: Ir≤2500A 0.33:Ir>2500A 1.25: Ir≤2500A 1.6: Ir>2500A 0.4: Ir≤2500A 0.5: Ir>2500A 1.25 |  |
| 9.6 | Maximum impact load during operative disconnector | kN | To be specified |  |
| 9.7 | Minimum air clearance in static state: - Between phase and earth - Between two poles/phase | mm | 2100 2100 |  |
| 10 | Material of main contact |  | Copper, copper alloy or aluminum alloy with silver/niken plated |  |
| 11 | Disconnector drive |  |  |  |
| 11.1 | Disconnector |  | Motor and Manual |  |
| 11.2 | Earthing switch |  | Motor and Manual |  |
| 12 | Local control cabinet for DS and ES: |  |  |  |
| 12.1 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) or steel hot dip galvanized with painted surface |  |
| 13.2 | Protection class |  | IP55 |  |
| 12.3 | Minimum cabinet thickness | mm | ≥ 2 |  |
| 12.4 | Number of limit switch contacts of the disconnector |  | ≥ (2NO+2NC) |  |
| 12.5 | Number of auxiliary contacts of DS |  | ≥ (12NO+12NC) |  |
| 12.6 | Number of spare auxiliary contacts of ES |  | ≥ (8NO+8NC) |  |
| 12.7 | Permissible long-term DC current of auxiliary contact | A | 10 |  |
| 12.8 | Short-time DC withstand current of auxiliary contact | A/ms | 100/30 |  |
| 12.9 | Lock of Remote/local control |  | Yes |  |
| 12.10 | Buttons for open/close of DS |  | Yes |  |
| 12.11 | Motor and MCB with separate power supply contacts for motor circuit |  | Yes |  |
| 12.12 | Equipped with overcurrent and overload protection for the motor |  | Yes |  |
| 12.13 | Drying system with temperature sensor, LED lighting, circuit breaker with separate auxiliary power contacts for drying and lighting circuits |  | Yes |  |
| 12.14 | Electrical interlocking for DS and ES |  | Yes |  |
| 13 | Operating voltage: |  |  |  |
| 13.1 | Voltage of DS, ES driver motor | VDC | 220 (+10%; -15%) |  |
| 13.2 | Voltage of DS & ES control | VDC | 220 (+10%; -15%) |  |
| 13.3 | Heating, lightning voltage | VAC | 220 (+10%; -15%) |  |
| 14 | Steel supporting structure hot dip galvanized |  | Manufacturer’s authorization letters |  |
| 14.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 14.2 | Material |  | Steel supporting structure hot dip galvanized |  |
| 15. | HV terminals connector: |  |  |  |
| 15.1 | Material |  | Aluminum alloy/copper |  |
| 15.2 | Dimensions |  | Suitable for designed conductor |  |
| 15.3 | Terminal clamping bolt |  | Stainless steel or other materials as required |  |
| 16 | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 17 | The remaining parameters or different will comply with the provisions of 271/QĐ-EVN, 91/QĐ-HDTV of EVN and 1676/QĐ-EVNNPT date 24/08/2025 of EVNNPT |  | Yes |  |
| 18 | Catalogues |  | To be supplied |  |
| 19 | Technical document |  | English/Vietnamese |  |

  - 110kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Technical parammeter: |  |  |  |
|  | Applicable standard |  | IEC 62271-102 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Method of neutral grounding |  | Directly earthed |  |
|  | Type |  | Outdoor |  |
| 4.1 | Configuration of one set |  | 1 phase/3 phase |  |
| 4.2 | Blade opening type |  | horizontal rotary |  |
| 4.3 | Number of earthing switches for the disconnector |  | 0 ES/ 1 ES/ 2 ES |  |
|  | Voltage parammeter of disconnector |  |  |  |
| 5.1 | Nominal voltage | kV | 110 |  |
| 5.2 | Max. operation voltage of systems | kV | 121 |  |
| 5.3 | Rated voltage | kV | 123 |  |
| 5.4 | Rated short-duration power-frequency withstand voltage + Phase-to-Earth + Across the isolating distance + Between phases | kV | 230 265 |  |
| 7.5 | Rated lightning impulse withstand voltage (1,2/50 µs-BIL) + Phase-to-Earth + Across the isolating distance + Between phases | kV peak | 550 630 |  |
|  | Current parammeter: |  |  |  |
| 6.1 | Rated normal current Ir | A | ≥ 2000 A (Coupler bay, tranfer bay and transformer bay); ≥ 1250 A (outgoing bay) |  |
| 8.2 | Short time withstand current | kArms | ≥ 50 |  |
| 8.3 | Rated duration of short-circuit | s | ≥ 1 |  |
| 8.4 | Rated peak withstand current | kA peak | ≥ 100 |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Technical parammeter of earthing switch: |  |  |  |
| 8.1 | Rated short-circuit making current | kA | 40 |  |
| 8.2 | Rated induced current of electrostatic coupling | Arms | Not applicable |  |
| 8.3 | Rated induced current of electromagnectic coupling | Arms | Not applicable |  |
| 8.4 | Rated withstand voltage between insulated terminals and bases earthed | kV | ≥ 160 |  |
|  | Operational capacity of disconnector and earthing switch: |  |  |  |
| 9.1 | Disconnector drive |  | 3 phases/single |  |
| 9.2 | Mechanical endurance class |  |  |  |
|  | Disconnector |  | M1 |  |
|  | Earthing switch |  | M0 |  |
| 9.3 | Total mechanical switching times, without maintenance |  |  |  |
|  | Disconnector | Times | ≥ 2000 |  |
|  | Earthing switch | Times | ≥ 1000 |  |
| 9.4 | Operation Tools for open/close DS and ES |  | Yes |  |
| 9.5 | Mechanical interlock between DS and ES |  | Yes |  |
|  | Total weight of 3-pole unit | kg | To be specified |  |
|  | Clearance: |  |  |  |
| 11.1 | Between phase and earth | mm | ≥ 1100 |  |
| 11.2 | Between two poles/phase | mm | ≥ 1100 |  |
|  | Support Insulator: |  |  |  |
| 12.1 | Applicable standard |  | According to IEC 60273 or equivalent |  |
| 12.2 | Material |  | Brown porcelain |  |
| 12.3 | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| 12.4 | Total minimum nominal specific creepage distance | mm | To be specified |  |
| 12.5 | Mechanical terminal load For three phases disconnector and earthing switch: - Straight load Fa1, Fa2 - Cross load Fb1, Fb2 For single phase disconnector and earthing switch: - Straight load Fa1, Fa2 - Cross load Fb1, Fb2 Vertical Force, Fc | kN | 0.5: Ir ≤1600A 0.6: Ir >1600A 0.17:Ir ≤1600A 0.2: Ir >1600A 0.8: Ir ≤1600A 1.0: Ir >1600A 0.2: Ir ≤1600A 0.3: Ir >1600A 1.0 |  |
| 12.6 | Maximum impact load during operative disconnector | kN | To be specified |  |
| 12.7 | Minimum air clearance in static state Between phase and earth Between two poles/phase | mm | ≥ 1100 ≥ 1100 |  |
|  | Material of main contact |  | Copper, copper alloy or aluminum alloy with silver/niken plated |  |
|  | Disconnector drive |  |  |  |
| 14.1 | Disconnector |  | Motor and Manual |  |
| 14.2 | Earthing switch |  | Motor and Manual |  |
| 15. | Local control cabinet for DS and ES: |  |  |  |
| 15.1 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) or steel hot dip galvanized with painted surface |  |
| 15.2 | Protection class |  | IP55 |  |
| 15.3 | Minimum cabinet thickness | mm | ≥ 2 |  |
| 15.4 | Number of limit switch contacts of the disconnector |  | ≥ (2NO+2NC) |  |
| 15.5 | Number of auxiliary contacts of DS |  | ≥ (8NO+8NC) |  |
| 15.6 | Number of spare auxiliary contacts of ES |  | ≥ (6NO+6NC) |  |
| 15.7 | Permissible long-term DC current of auxiliary contact | A | 10 |  |
| 15.8 | Short-time DC withstand current of auxiliary contact | A/ms | 100 /30 |  |
| 15.9 | Lock of Remote/local control |  | Yes |  |
| 15.10 | Buttons for open/close of DS |  | Yes |  |
| 15.11 | Motor and MCB with separate power supply contacts for motor circuit |  | Yes |  |
| 15.12 | Equipped with overcurrent and overload protection for the motor |  | Yes |  |
| 15.13 | Drying system with temperature sensor, LED lighting, circuit breaker with separate auxiliary power contacts for drying and lighting circuits |  | Yes |  |
| 15.14 | Electrical interlocking for DS and ES |  | Yes |  |
| 16. | Operating voltage: |  |  |  |
| 16.1 | Voltage of DS, ES driver motor | VDC | 220 (+10%; -15%) |  |
| 16.2 | Voltage of DS & ES control | VDC | 220 (+10%; -15%) |  |
| 16.3 | Heating, lightning voltage | VAC | 220 (+10%; -15%) |  |
| 17 | Steel supporting structure hot dip galvanized |  | Manufacturer’s authorization letters |  |
| 17.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 17.2 | Material |  | Steel supporting structure hot dip galvanized |  |
| 18 | HV terminals connector: |  |  |  |
| 18.1 | Material |  | Aluminum alloy/copper |  |
| 18.2 | Dimensions |  | Suitable for designed conductor |  |
| 18.3 | Terminal clamping bolt |  | Stainless steel or other materials as required |  |
| 19 | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 20 | The remaining parameters or different will comply with the provisions of 271/QĐ-EVN, 91/QĐ-HDTV of EVN and 1676/QĐ-EVNNPT date 24/08/2025 of EVNNPT |  | Yes |  |
| 21 | Catalogues |  | To be supplied |  |
| 22 | Technical document |  | English/Vietnamese |  |

22kV Disconnector and Earthing switch

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 62271-102 |  |
|  | Type |  | Outdoor, center-break, 3 poles, horizontal rotary |  |
|  | Disconnector drive type |  | Three phase |  |
|  | Material of main contact |  | Copper alloy or aluminum alloy with silver/niken plated |  |
|  | Disconnector drive |  |  |  |
| 8.1 | Disconnector |  | Motor and Manual |  |
| 8.2 | Earthing switch |  | Motor and Manual |  |
|  | Nominal voltage | kV | 22 |  |
|  | Rated voltage | kV | ≥ 24 |  |
|  | Rated current | A | ≥ 630 |  |
|  | Frequency | Hz | 50 |  |
|  | Short time withstand current (1 sec.) of DS and ES | kArms | ≥ 25 |  |
|  | Rated peak withstand current | kA peak | ≥ 62,5 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Lighting impulse voltage (1.2/50µs) withstand of disconnector: |  |  |  |
| 15.1 | Phase to earth | kV peak | ≥ 125 |  |
| 15.2 | Across open disconnector | kV peak | ≥ 125 |  |
|  | Power frequency withstand voltage |  |  |  |
| 16.1 | Phase - Earth | kV rms. | ≥ 50 |  |
| 16.2 | Across open disconnector | kV rms. | ≥ 50 |  |
|  | Resistance of main contact (new contact) | µΩ | To be specified |  |
|  | Support Insulator: |  |  |  |
| 19.1 | Applicable standard |  | To be specified |  |
| 19.2 | Type |  | To be specified |  |
| 19.3 | Material |  | Brown porcelain |  |
| 19.4 | Minimum nominal creepage distance | mm/kV | 31 |  |
| 19.5 | Total minimum nominal specific creepage distance | mm | To be specified |  |
| 19.6 | Rated static mechanical terminal load: |  |  |  |
| - | Straight load | kN | Comply with IEC 62271-102 |  |
| - | Cross load | kN |  |  |
| - | Vertical load | kN |  |  |
| 19.7 | Clearance: |  |  |  |
|  | Between phase and earth | mm | Comply to IEC 60071-1 |  |
|  | Between poles (phase to phase) | mm | Comply to IEC 60071-1 |  |
|  | Between two poles/phase | mm | To be specified |  |
|  | Distance between phase (close position) | mm | To be specified |  |
|  | Operating voltage |  |  |  |
| 20.1 | Rating voltage of DS driver motor | VDC | 220 (+10%; -15%) |  |
| 20.2 | Heating voltage | VAC | 220 (+10%; -15%) |  |
| 20.3 | Rating voltage of DS & ES control, interlocking coil | VDC | 220 (+10%; -15%) |  |
|  | Operation Tools for open/close DS and ES |  | Yes |  |
|  | Mechanical interlock between DS and ES |  | Yes |  |
|  | Operation DS and ES (not use counterweight) |  | Comply |  |
|  | Total weight of 3-pole unit | kg | To be specified |  |
|  | Local control cabinet for DS and ES |  |  |  |
| 25.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 25.2 | Place of factory |  | To be specified |  |
| 25.3 | Designation |  | To be specified |  |
| 25.4 | Material of cabinet |  | Aluminium alloy (Al Mg3 H22) or stainless steel (Inox-304) |  |
| 25.5 | Protection class |  | IP55 |  |
| 25.6 | Number of spare auxiliary contacts of DS (Repeating aux. switch contact via aux. contactor or aux. relay shall be not accepted) |  |  |  |
| - | Limit switch normally opened contact |  | ≥ 2 |  |
| - | Limit switch normally closed contact |  | ≥ 2 |  |
| 25.7 | Number of auxiliary contacts of DS: |  |  |  |
| - | Normally opened contact |  | ≥ 10 |  |
| - | Normally closed contact |  | ≥ 10 |  |
| 25.8 | Number of spare auxiliary contacts of ES (Repeating aux. switch contact via aux. contactor or aux. relay shall be not accepted) |  |  |  |
| - | Normally opened contact |  | ≥ 4 |  |
| - | Normally closed contact |  | ≥ 4 |  |
| 25.9 | Lock of Remote/local control |  | Yes |  |
| 25.10 | Buttons for open/close of DS, ES |  | Có |  |
| 25.11 | Motor and MCB with separate power supply contacts for motor circuit |  | Yes |  |
| 25.12 | MCB for power-supply of drying and lighting has separate contact. |  | Yes |  |
| 25.13 | Overcurrent and overload protection circuit for the motor |  | Yes |  |
| 25.14 | Electrical interlocking for DS and ES |  | Yes |  |
|  | Steel supporting structure hot dip galvanized |  | Manufacturer’s authorization letters |  |
| 26.1 | Manufacturer/Country of Origin |  | To be specified |  |
| 26.2 | Material |  | To be specified |  |
|  | HV terminals connector: |  |  |  |
| 27.1 | Material |  | Aluminum alloy/copper |  |
| 27.2 | Dimensions |  | Suitable for designed conductor |  |
| 27.3 | Holes - No. , size and spacing |  | To be specified |  |
| 27.4 | Number holes (min 6 holes) or stud type |  | Comply |  |
|  | When the DS is closed, the contacts do not form a hole for the bird to nest |  | Yes |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | Technical document |  | English/Vietnamese |  |

Other requirements of goods eligibility:

All Disconnector and Earthing (Designation HCB) from Siemens - India shall not be allowed for bid according to EVNNPT official document No. 3140/EVNNPT-KT + PC + ĐT + QLĐT+ QLXD, dated 11/09/2019).

- CURRENT TRANSFORMER

  - 220kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60044-1, 2 IEC 61869-1, 2 |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, Top core, reinforce safety design |  |
|  | Rated voltage | kV | ≥ 245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | ≥ 1050 |  |
|  | Power Frequency Voltage withstand |  |  |  |
| - | Primary windings | kV | ≥ 460 |  |
| - | Secondary windings | kV | 3 |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| - | Total minimum nominal specific creepage distance | mm | ≥ 7595 |  |
| - | Average diameter of insulator |  | To be specified |  |
|  | Rated Primary Current | A | 2000/3000 |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Extended Current Rating |  | 120% of Rated |  |
|  | Rated Transformation Ratios | A |  |  |
| - | Type 1 (Outgoing bay and transformer bay) | A | 800-1200-2000/1/1/1/1/1 |  |
| - | Type 2 (Tranfer bay) | A | 1200-2000-3000/1/1/1/1/1 |  |
| - | Type 3 (Coupling bay and Huang Qiao outgoing bay) | A | 1200-2000-3000/1/1/1/1/1/1 |  |
|  | Rated Thermal Withstand Current (1 sec.) | kA | ≥ 50 |  |
|  | Rated Dynamic Withstand Current | kA | ≥125 |  |
|  | Operating time of CT |  |  |  |
| - | Total operating time until maintain | Year | ≥ 8 |  |
| - | Total operating time until replacement | Year | ≥ 20 |  |
|  | Maximum Partial Discharge Level at 1.1 Un (highest system voltage) | pC | To be specified |  |
|  | Secondary Winding Resistance | Ω | To be specified |  |
|  | Terminals |  |  |  |
| - | Materials |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Total Weight | kg | To be specified |  |
|  | Calculated Wind Load Moment about Base | kN | To be specified |  |
|  | Core Characteristics: Rated Burden, Accuracy Class |  |  |  |
|  | Type 1 |  |  |  |
| - | Core No. 1, 4, 5 |  | 30VA - Cl 5P20 |  |
| - | Core No. 2, 3 |  | 10VA - Cl 0.5 |  |
|  | Type 2 |  |  |  |
| - | Core No. 1, 4, 5 |  | 30VA - Cl 5P20 |  |
| - | Core No. 2, 3 |  | 10VA - Cl 0.5 |  |
|  | Type 3 |  |  |  |
| - | Core No. 1, 5, 6 |  | 30VA - Cl 5P20 |  |
| - | Core No. 2 |  | 10VA - Cl 0.2s |  |
| - | Core No. 3, 4 |  | 10VA - Cl 0.5 |  |
|  | All burdens, accuracy Classes at all ratios |  | Yes |  |
|  | Limits of current error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11, IEC 60044-1 or Table 201, IEC 61869-2 |  |
| - | For secondary windings with class 5P20 (at 25%÷100% Rated Burden) |  | Comply with: Table 14, IEC 60044-1 or Table 205, IEC 61869-2 |  |
|  | Multi-Ratio shall be changed on secondary winding |  | Yes |  |
|  | Approved by STAMEQ |  | As Sope of Supply |  |
|  | Temperature rise | 0C | 65 |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1819/QĐ-EVNNPT date 16/09/2025 |  | Yes |  |

  - 110kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | General specifications |  | Comply |  |
|  | Applicable standard |  | IEC 61869-1, 2 or equivalent |  |
|  | Type |  | Outdoor, Single phase, oil paper immersed, Top core, reinforce safety design |  |
|  | Rated voltage of electrical system | kV | 110 |  |
|  | Rated voltage | kV | ≥ 123 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | ≥550 |  |
|  | Power Frequency Voltage withstand |  |  |  |
| - | Primary windings | kV | ≥230 |  |
| - | Secondary windings | kV | ≥3 |  |
|  | Phase to Earth Clearance | mm | ≥ 1100 |  |
|  | Rated Primary Current |  |  |  |
|  | Type 1 (Transformer bay, Transfer bay) | A | 800-1600-2000/1/1/1/1/1A |  |
| - | Type 2 (Coupling bay) | A | 800-1200-1600-2000/1/1/1/1/1A |  |
| - | Type 3 (Outgoing bay) | A | 400-800-1200/1/1/1/1/1A |  |
|  | Rated Transformation Ratios |  |  |  |
| - | Type 1, type 2 | A | 2000 |  |
| - | Type 3 | A | 1200 |  |
|  | Rated Thermal Withstand Current (1 sec.) | kA | 40 |  |
|  | Rated duration of short-circuits | sec | ≥ 1 |  |
|  | Continuous overcurrent capability |  | ≥ 1.2 Ipr |  |
|  | Rated Dynamic Withstand Current | kA | ≥ 100 |  |
|  | Maximum Partial Discharge Level at 1.1 Un (highest system voltage) | pC | ≤ 10 |  |
|  | Secondary Winding Resistance | Ω | To be specified |  |
|  | Tanδ (dielectric loss) measured at 50Hz performed on complete CT |  |  |  |
| 21.1 | At the factory made by the manufacturer (Routine test) |  | ≤ 0.5% |  |
| 21.2 | On site after complete installation |  | ≤ 0.5% |  |
|  | Oil level indicator CT |  | Yes |  |
|  | Core Characteristics: Rated Burden, Accuracy Class |  |  |  |
|  | Type 1, 2, 3 |  |  |  |
|  | Core No. 3, 4, 5 |  | 20VA - Cl 5P20 |  |
|  | Core No. 1, 2 |  | 10VA - Cl 0.5 |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized sheet steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. IP55 |  |
|  | Change ratio of variable CT |  | Change at the secondary coil |  |
|  | Total Weight | kg | To be specified |  |
|  | Label parameters |  | According to IEC 61869-1, - 2 or equivalent |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| - | Total minimum nominal specific creepage distance | mm | ≥ 3813 |  |
| - | Calculated Wind Load Moment about Base | kN | To be specified |  |
|  | Terminals |  | To be specified |  |
| - | Materials |  | To be specified |  |
| - | Dimensions |  | To be specified |  |
| - | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Operating conditions |  | Complete Bidding document |  |
|  | Steel supporting structure hot dip galvanized |  | As Scope of supply |  |
| - | Manufacturer/Country of Origin |  |  |  |
| - | Material |  |  |  |
|  | Technical document |  | English/Vietnamese |  |
|  | Product quality management standards |  | ISO 9001:2015 or equivalent |  |
|  | Temperature rise | oC | ≤65 |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | Approved by STAMEQ for all CTs |  | As Sope of Supply |  |
|  | The remaining parameters or different will comply with the provisions of 105/QĐ-HĐTV of EVN |  | Yes |  |

  - 22kV Current Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-1, 2 or TCVN 11845-2 or TCVN 7697-1 or equivalent |  |
|  | Type |  | Outdoor, single phase, oil paper immersed or Epoxy resin molded resin |  |
|  | Rated voltage | kV | 24 |  |
|  | Neutral point operating |  | Direct grounding |  |
|  | Frequency | Hz | 50 |  |
|  | Rated Primary Current | A |  |  |
|  | Type 1 | A | 1200-2000 |  |
|  | Type 2 | A | 50-100 |  |
|  | Rated Secondary Current | A | 1 |  |
|  | Continuous overcurrent capability |  | ≥ 1.2 Ir |  |
|  | Rated Thermal Withstand Current (1 sec.) | kA | ≥ 25 |  |
|  | Rated Dynamic Withstand Current | kA | ≥ 62.5 |  |
|  | Rated Transformation Ratios |  |  |  |
|  | Type 1 |  | 1200-2000/1A |  |
|  | Type 2 |  | 50-100/1/1A |  |
|  | Core Characteristics: Rated Burden, Accuracy Class |  |  |  |
|  | Type 1: |  |  |  |
|  | Core No. 1 |  | 20VA - Cl 5P20 |  |
|  | Type 2: |  |  |  |
|  | Core No. 1 |  | 10VA - Cl 0.5 |  |
|  | Core No. 2 |  | 20VA - Cl 5P20 |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | ≥ 125 |  |
|  | Power Frequency Voltage withstand on Primary windings | kV | ≥ 50 |  |
|  | Power Frequency Voltage withstand on Secondary windings | kV | ≥ 3 |  |
|  | Partial discharge level: limit shall not be exceeded at the partial discharge test voltage 1.2xUm/√3 |  |  |  |
|  | - Solid insulation | pC | 20 |  |
|  | - Immersion in liquid | pC | 5 |  |
|  | Temperature rise | oC | ≤60 |  |
|  | Housing insulator: |  |  |  |
|  | Applicable standard |  | To be specified |  |
|  | Material |  | Brown porcelain |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Total minimum nominal specific creepage distance | mm | ≥ 744 |  |
| - \ | Oil level indicator, oil drain valve (applicable to current transformers immersed in oil) |  | Yes |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized sheet steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. IP55 |  |
|  | Connector label |  | The connector label shall allow identification of: - Primary and secondary coils. - Sections of the coil (if any). - The relevant polarity of the coils and windings. - Intermediate steps (if any). Terminals shall be clearly and conspicuously marked on the surface or in the vicinity of the connector. This labeling must include: - The letters are placed after or before the numbers. The letters must be capital letters. - The symbols of the current transformer terminals shall comply with the relevant TCVN or IEC standards. |  |
|  | Label for device |  | Current transformers must have a label permanently attached to the body with the following minimum contents: - Manufacturer's name or other mark which allows for easy identification of the manufacturer. - Code, Serial number. - Year of manufacture. - Rated primary and secondary currents. - Rated frequency. - Rated power and accuracy grade. - Maximum voltage of the device. - Rated insulation level - Thermal stability current (Ith) and dynamic stabilizing current (Idyn) (if different 2.5 times Ith). - Insulation class (if different from class A). All information is guaranteed not to fade over operating life |  |
|  | Total Weight | kg | To be specified |  |
|  | Terminals |  |  |  |
|  | Material |  | To be specified |  |
|  | Dimensions |  | To be specified |  |
|  | Number of hole (minimum 6 holes) |  | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 330 |  |
|  | Approved by STAMEQ for all CTs |  | As Sope of Supply |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 105/QĐ-HĐTV of EVN |  | Yes |  |

- VOLTAGE TRANSFORMER

- 220kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 6044-1, 5 IEC 61869-1, 5 |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, reinforce safety design with steel tank |  |
|  | Rated voltage | kV | ≥ 245 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥ 1050 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥ 460 |  |
| - | Secondary windings | kV | ≥ 3 |  |
|  | Rated Maximum HF Current | A | To be specified |  |
|  | Temperature Co-efficient of capacitance per oC |  | To be specified |  |
|  | Maximum Partial/Discharge Level .pC | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
| - | Applicable standard |  | To be specified |  |
| - | Material |  | Brown porcelain |  |
| - | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
| - | Minimum nominal specific creepage distance | mm | ≥ 7595 |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Rated Mechanical Terminal Load | kN | To be specified |  |
|  | Facilities for fitting of line trap |  | If any |  |
|  | Max. Permissible Top Wind Loading | km/hr | To be specified |  |
|  | Calculated Wind Load Moment about Base | kNm | To be specified |  |
|  | HV Terminals |  | To be specified |  |
| - | Material |  |  |  |
| - | Dimensions |  |  |  |
| - | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Flux Density at Rated Voltage | Tesla | To be specified |  |
|  | Recommended Fuse Ratings |  | To be specified |  |
|  | Weight of Intermediate Voltage Transformer | kg | To be specified |  |
|  | Oil outlet and oil test valve |  | Yes |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | Type 1 |  |  |  |
| - | Winding No.1 |  | 220kV:√3 /110V:√3 25VA - Cl 0.5 |  |
| - | Winding No.2 |  | 220kV:√3 /110V:√3 50VA - Cl 3P |  |
|  | Type 1 |  |  |  |
|  | Winding No.1 |  | 220kV:√3 /110V:√3 25VA - Cl 0.2 |  |
|  | Winding No.2 |  | 220kV:√3 /110V:√3 25VA - Cl 0.5 |  |
|  | Winding No.3 |  | 220kV:√3 /110V:√3 50VA - Cl 3P |  |
|  | Maximum simultaneous burden output/ accuracy class |  | 25VA for class 0.2 25VA for class 0.5 50VA for class 3P |  |
|  | Limits of voltage error and phase displacement |  |  |  |
| - | For secondary windings with class 0.5 (at 25%÷100% Rated Burden) |  | Comply with: Table 11, IEC 60044-2 or Table 501, IEC 61869-5 |  |
| - | For secondary windings with class 3P (at 25%÷100% Rated Burden) |  | Comply with: Table 12, IEC 60044-2 or Table 502, IEC 61869-5 |  |
|  | Approved by STAMEQ for all CVTs |  | As Sope of Supply |  |
|  | Over volt capability |  |  |  |
| - | Continuous |  | 1.2x220kV/√3 |  |
| - | 30 sec |  | 1.5x220kV/√3 |  |
|  | Temperature rise | 0C | ≤ 65 |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 1816/QĐ-EVNNPT date September, 09,2025 |  | Yes |  |

- 110kV Capacitor Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | General Specifications |  | Comply Bidding document |  |
|  | Applicable standard |  | IEC 61869-1, 5 or equivalent |  |
|  | Type |  | Outdoor, single phase, oil paper immersed, reinforce safety design with steel tank |  |
|  | Insulating porcelain body |  | Seamless, No joints |  |
|  | Rated system voltage | kV | 110 |  |
|  | Rated voltage | kV | ≥ 123 |  |
|  | Frequency | Hz | 50 |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥ 550 |  |
|  | Power Frequency Voltage Withstand |  |  |  |
| - | Primary windings | kV rms. | ≥ 230 |  |
| - | Secondary windings | kV | ≥ 3 |  |
|  | Phase to Earth Clearance | mm | ≥1100 |  |
|  | Over volt capability |  |  |  |
|  | Continuous |  | 1.2x110kV/√3 |  |
|  | 30 sec |  | 1.5x110kV/√3 |  |
|  | Rated capacitance | pF | To be specified |  |
|  | Rated capacitance guarantee limit |  | To be specified |  |
|  | Maximum partial discharge at maximum system voltage | pC | ≤ 10 |  |
|  | Magnetic flux density at rated voltage | Tesla | To be specified |  |
|  | Tanδ (dielectric loss) measured at 50Hz |  |  |  |
|  | a. At the factory, performed by the Manufacturer on the complete CVT, on the voltage divider and on the electromagnetic converter before delivery (routine test) ensure the following values: | % |  |  |
|  | - Voltage division capacitor |  | ≤ 0.5 |  |
|  | - Electromagnetic converter |  | To be specified |  |
|  | - Complete CVT set |  | ≤ 1 |  |
|  | - On site after complete instalation | % | ≤ 1 |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | Winding No.1 |  | 110kV:√3 /110V:√3 15VA - Cl 0.5 |  |
|  | Winding No.2 |  | 110kV:√3 /110V:√3 15VA - Cl 0.5 |  |
|  | Winding No.3 |  | 110kV:√3 /110V:√3 50VA - Cl 3P |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. IP55 |  |
|  | Oil level indicator and oil valve |  | Yes |  |
|  | Label parameters |  | According to IEC 61869-1, - 2 or equivalent |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Housing insulator: |  |  |  |
|  | Applicable standard |  | To be specified |  |
|  | Material |  | Brown porcelain |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Minimum nominal specific creepage distance | mm | ≥ 3813 |  |
|  | Mechanical load capacity | kN | To be specified |  |
|  | Steel supporting structure hot dip galvanized |  | As Scope of supply |  |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Material |  | To be specified |  |
|  | HV Terminals |  | To be specified |  |
|  | Material |  |  |  |
|  | Dimensions |  |  |  |
|  | Number of hole (minimum 6 holes) or stud type |  | To be specified |  |
|  | Operating conditions |  | Complete Bidding document |  |
|  | Technical document |  | English/Vietnamese |  |
|  | Product quality management standards |  | ISO 9001:2015 or equivalent |  |
| - - | Temperature rise | oC | ≤65 |  |
| - - | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| - - | Catalogues |  | To be supplied |  |
| - - | Approved by STAMEQ for all CVTs |  | As Sope of Supply |  |
| - - | The remaining parameters or different will comply with the provisions of 104/QĐ-HĐTV of EVN |  | Yes |  |

Notes:

All 220kV, 110kV CVT from ABB - INDIA shall not be eligible (EVNNPT has declared that all equipment 220kV, 110kV CVT (WP 245 N2 and WN 145 N2) from ABB-India shall not be allowed for bid according to EVNNPT official document No. 1762/EVNNPT-KT, dated 19/05/2021;

- 22kV Voltage Transformer

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-1, -3 or TCVN 11845-3 or TCVN 7697-2 or equivalent |  |
|  | Type |  | Outdoor, voltage transformer, single phase, oil immersed or epoxy resin |  |
|  | Rated voltage | kV | 24 |  |
|  | Rated voltage on primary winding | kV | 22/√3 |  |
|  | Rated voltage on Secondary winding | V | 110/√3 |  |
|  | Neutral point operating |  | Direct grounding |  |
|  | Frequency | Hz | 50 |  |
|  | Voltage ratio, burden, accuracy class |  |  |  |
|  | Winding No.1 |  | 22:√3 /0.11:√3kV 15VA - Cl 0.5 |  |
|  | Winding No.2 |  | 22:√3 /0.11:√3kV 15VA - Cl 3P |  |
|  | Winding No.3 |  | 22:√3 /0.11:3kV 15VA - Cl 3P |  |
|  | Impulse Voltage (1.2/50µs) Withstand | kV peak | ≥ 125 |  |
|  | Power Frequency Voltage Withstand on Primary windings (1 min) | kV rms. | ≥ 50 |  |
|  | Power Frequency Voltage Withstand on Secondary windings (1 min) | kV | ≥ 3 |  |
|  | Over volt capability |  |  |  |
|  | Continuous |  | 1.2 |  |
|  | 30s |  | 1.5 |  |
|  | Partial discharge level: limit shall not be exceeded at the partial discharge test voltage 1.2xUm/√3 |  |  |  |
|  | - Solid insulation | pC | 20 |  |
| - | - Immersion in liquid | pC | 5 |  |
|  | Temperature rise | oC | 60 |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Total Minimum nominal specific creepage distance |  | ≥ 744 |  |
|  | Oil outlet and oil test valve (applicable to voltage transformers immersed in oil) |  | Yes |  |
|  | Second terminal box cover design, lead hole |  | - The secondary terminal cover is made of aluminum, aluminum alloy, stainless steel or hot-dip galvanized sheet steel. - The lid of the box or the base of the box and the bolts of the lid must have holes drilled to thread the sealing lead. |  |
|  | Connector label |  | The connector label shall allow identification of: - Primary and secondary coils. - Parts of the coil (if any). - The relevant poles of the coil and the coil. - Intermediate steps (if any). Terminals shall be clearly and conspicuously marked on the surface or vicinity of the connector. This labeling must include: - The letters are placed after or before the numbers. The letters must be capital letters. - Symbols of voltage transformer terminals shall be in accordance with relevant TCVN or IEC standards |  |
|  | Label for device |  | Votage transformers must have a label permanently attached to the body with the following minimum contents: - Manufacturer's name or other mark which allows for easy identification of the manufacturer. - Code, Serial number. - Year of manufacture. - Rated primary and secondary Voltage. - Rated frequency. - Rated power and accuracy grade. - Maximum voltage of the device. - Rated insulation level - Overvoltage factor over time. - Insulation class (if different from class A). All information is guaranteed not to fade over operating life |  |
|  | Approved by STAMEQ for all VTs |  | As Sope of Supply |  |
|  | HV Terminals |  | To be specified |  |
|  | Material |  |  |  |
|  | Dimensions |  |  |  |
|  | Number of hole |  | To be specified |  |
|  | Weight of capacitor voltage transformer | kg | To be specified |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be specified |  |
|  | The remaining parameters or different will comply with the provisions of 104/QĐ-HĐTV of EVN |  | Yes |  |

- SURGE ARRESTER

  - 220kV Surge Arrester

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/Country of Origin |  | To be specified |  |
|  | Model type |  | To be specified |  |
|  | Standards for manufacturing and testing |  | To be specified |  |
|  | Rated frequency | Hz | 50 |  |
|  | Nominal system voltage | kV | 220 |  |
|  | Maximum required working voltage for equipment | kV | 245 |  |
|  | Neutral grounding |  | Direct |  |
|  | Allowable overvoltage factor when single phase grounding |  | 1.4 |  |
|  | Lightning arrester connection mode |  | phase - earth |  |
|  | Technical parameters of Surge Arrester |  |  |  |
| 10.1 | Type |  | Outdoor, ZnO, gapless |  |
| 10.2 | Rated voltage Ur | kV | ≥ 192 |  |
| 10.3 | Continuous Operating voltage Ucov | kV | ≥ 152 |  |
| 10.4 | emporary overvoltage with TOV characteristic curve | kVrms | Meet regional grid configuration |  |
| 10.5 | Nominal Discharge Current-In | kA | ≥ 10 |  |
| 10.6 | Peak discharge current | kApeak | ≤ 100 |  |
| 10.7 | Rated thermal energy absorption level Wth according to Ur | kJ/kV | ≥ 7 |  |
| 10.8 | Repeatable launch capability - Qrs | C | ≥ 1.6 |  |
| 10.9 | Equipotential - Ring |  | To be specified |  |
|  | Technical specifications of Housing surge Arrester |  |  |  |
| 11.1 | Materials for manufacturing housing surge Arrester |  | Porcelain or Polymer |  |
| 11.2 | Rated short-duration power-frequency withstand voltage |  | ≥460 |  |
| 11.3 | Rated lightning impulse withstand voltage |  | ≥1050 |  |
| 11.4 | Creepage distance of insulation | mm/kV | ≥ 31 |  |
| 11.5 | Short circuit withstand capacity | kA | ≥50 |  |
| 11.6 | Specified long term load | N | ≥ 400 |  |
| 11.7 | Specified short term load | N | ≥ 1000 |  |
| 11.8 | Mean breaking load | N | ≥1200 |  |
|  | Accessories of Surge Arrester |  |  |  |
|  | Lightning counter with leakage current display |  | Yes |  |
| 12.1 | Number of digits of lightning counter |  | ≥ 5 |  |
| 12.2 | Leakage current measuring range | mA | To be specified |  |
| 12.3 | Sensitivity to lightning surges | A | ≤ 200 |  |
| 12.4 | Current pulse withstand capability (4/10 μs) | kA | ≥ 100 |  |
| 12.5 | Minimum protection level of lightning arrester enclosure |  | IP 54 |  |
|  | Surge Arrester support material (if any) |  | Galvanized steel with minimum coating thickness of 80μm |  |
|  | HV terminal connector |  | 01 terminal connector/01 Surge Arrester |  |
| 14.1 | Material |  | Suitable for design conductors |  |
| 14.2 | size |  | Suitable for design conductors |  |
| 14.3 | bolt |  | Stainless steel or hot-dip galvanized |  |
|  | The accompanying technical documents clearly show the bidding parameters, dimensional drawings, installation, operation and maintenance instructions. |  | Yes |  |
|  | The remaining parameters or different will comply with the provisions of 1158/QĐ-EVNNPT of EVNNPT and 2416/QĐ-EVNNPT of EVNNPT |  | Yes |  |

  - 110kV Surge Arrester

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60099-4 |  |
|  | Maximum operating voltage of the electrical system | kV | 123 |  |
|  | Rated frequency | Hz | 50 |  |
|  | Operating mode of the system |  | Directly grounded neutral |  |
|  | Type |  | Outdoor, ZnO, gapless, according to IEC |  |
|  | Rated voltage (Ur) | kV | ≥ 96 |  |
|  | Maximum continuous operating voltage (UC) | kV | ≥ 77 |  |
|  | Temporarily overvoltage voltage with TOV characteristic curve | kVrms | To be specified |  |
|  | Nominal discharge current | kA | 10 |  |
|  | Peak discharge current | kApeak | 100 |  |
|  | Minimum energy absorption capability | kJ/kV (Ur) | ≥ 7 |  |
|  | Qrs Repeatability | C | ≥ 1.6 |  |
|  | Insulation coordination coefficient |  | ≥ 1.4 |  |
|  | Rated insulation level |  |  |  |
| - | Lightning impulse withstand voltage | kVrms | ≥ 550 |  |
| - | Power frequency withstand voltage | kVp | ≥ 230 |  |
|  | Short circuit current | kA | ≥ 40 |  |
|  | Static load capacity | kN | To be specified |  |
|  | Dynamic load capacity | kN | To be specified |  |
|  | IEC long duration discharge class |  | 3 |  |
|  | Maximum residual voltage of complete arrester for: |  |  |  |
|  | Steep impulse | kV | ≤ 2.8 x Ur |  |
|  | Lightning impulse | kV | ≤ 2.5 x Ur |  |
|  | Switching impulse | kV | ≤ 2.1 x Ur |  |
|  | Lightning counter with leakage current display |  | To be specified |  |
| - | Manufacture/ Country of Origin |  | To be specified |  |
| - | Place of factory |  | To be specified |  |
| - | Designation |  | To be specified |  |
| - | Leakage current measurement range: 0-30mA |  | Yes |  |
| - | Number of digits of lightning counter |  | ≥ 5 |  |
| - | Sensitivity of lightning impulse |  | ≤ 200 |  |
| - | Impulse withstand capacity power (4/10 μs) | kA | ≥ 100 |  |
| - | Protection level |  | IP54 |  |
|  | Arrester housing: |  |  |  |
|  | Material |  | Silicon rubber or porcelain |  |
|  | Lightning impulse withstand | kV | To be specified |  |
|  | Switching impulse withstand | kV | To be specified |  |
|  | Power frequency withstand | kVrms. | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |
|  | Total minimum nominal specific creepage distance | mm | ≥ 3813 |  |
|  | Terminal materials |  |  |  |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Material |  | Suitable for the conductor |  |
|  | Dimensions |  | Suitable for the conductor |  |
|  | Terminal clamp bolt |  | Stainless steel or hot-dip galvanized steel |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Technical document |  | English/Vietnamese |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 110/QĐ-HĐTV of EVN |  | Yes |  |

  - 22kV Surge Arrester

| Item No | Description | Unit | Required | Offered |  |
| --- | --- | --- | --- | --- | --- |
| I | General information about the manufacturer |  |  |  |  |  |
| 1 | Manufacturer |  | To be specified |  |  |
| 2 | Country of Origin/ Year |  | To be specified |  |  |
| 3 | Code |  | To be specified |  |  |
| 4 | Applicable standard |  | IEC 60099-4 |  |  |
| II | System service conditions |  |  |  |  |  |
| 1 | Maximum operating voltage | kV | 24 |  |  |
| 2 | frequency | Hz | 50 |  |  |
| 3 | Method of neutral earthing |  | Directly grounded neutral |  |  |
| 4 | Connection mode for surge arresters |  | Phase- earth |  |  |
| III | Technical specifications of surge arresters |  |  |  |  |  |
| 1 | Type |  | Outdoor, ZnO, gapless |  |  |
| 2 | Discharge class |  | SM or higher |  |  |
| 3 | Rated voltage Ur | kV | ≥ 30 |  |  |
| 4 | Maximum continuous operating voltage COV (UC) | kVrms | ≥ 24 |  |  |
| 5 | Temporary overvoltage along with the TOV characteristic curve | kVrms | To be specified |  |  |
| 6 | Nominal discharge current | kA | ≥ 10 |  |  |
| 7 | Peak discharge current | kApeak | ≥ 100 |  |  |
| 8 | Minimum energy absorption capability Wth | kJ/kV*Ur | ≥ 4 |  |  |
| 9 | Repetitive Flashover Capability - Qrs | C | ≥ 1 |  |  |
| 10 | Insulation Coordination Factor |  | ≥ 1.3 |  |  |
| IV | Arrester housing: |  |  |  |  |  |
| 1 | Material |  | Silicon rubber (SR)/polymer or porcelain |  |  |
| 2 | Rated lightning impulse withstand voltage (1.2/50 µs-BIL) | kV | ≥ 125 |  |  |
| 3 | Power frequency withstand voltage, 60s | kV | ≥ 50 |  |  |
| 4 | Minimum nominal creepage distance | mm/kV | ≥ 31 |  |  |
| 5 | Short circuit current | kA | ≥ 25 |  |  |
| 6 | Static load capacity | kN | To be specified |  |  |
| 7 | Dynamic load capacity | kN | To be specified |  |  |
| V | Other accessories |  |  |  |  |  |
| 1 | Lightning counter with leakage current display |  | Yes |  |  |
|  | Manufacturer/ Country of Origin |  | To be specified |  |  |
|  | Code |  | To be specified |  |  |
|  | Leakage Current Range: 0 - 30mA |  | Yes |  |  |
|  | Number of digits of lightning counter |  | ≥ 5 |  |  |
|  | Sensitivity of lightning impulse | A | ≤ 200 |  |  |
|  | Impulse withstand capacity power (4/10 μs) | kA | ≥ 100 |  |  |
|  | Protection level |  | IP54 |  |  |
| 2 | Terminal materials |  |  |  |  |
|  | Manufacturer/ Country of Origin |  | To be specified |  |  |
|  | Material |  | Suitable for the conductor |  |  |
|  | Dimensions |  | Suitable for the conductor |  |  |
|  | Terminal clamp bolt |  | stainless steel or hot-dip galvanized steel |  |  |
| VI | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |  |
| VII | Technical document |  | English/Vietnamese |  |  |
| VIII | Catalogues |  | To be supplied |  |  |
| IX | The remaining parameters or different will comply with the provisions of 110/QĐ-HĐTV of EVN |  | Yes |  |  |

- 110KV CAPACITOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | General requirement from power system |  |  |  |
|  | Maximum system operating voltage | kV | 121 |  |
|  | Minimum system operating voltage | kV | 99 |  |
|  | Nominal system voltage | kV | 110 |  |
|  | Nominal frequency | Hz | 50 |  |
|  | Rated three phase symmetrical short-circuit breaking current | kA | 40 |  |
|  | Rated duration of short-circuit | sec | 1 |  |
|  | Lightning impulse withstand voltage | kVpeak | > 550 |  |
|  | Power frequency withstand voltage (1 min. 50 Hz) | kVrms | > 230 |  |
|  | Connection diagram |  | 3 phase 3 wire |  |
|  | Neutral grounding mode |  | Direct |  |
|  | Ground fault factor of transmission grid |  | ≤ 1.4 |  |
| 2 | Capacitor unit |  |  |  |
|  | Manufacturer/Country of Origin |  | offered by Tender |  |
|  | Year of manufacture |  | offered by Tender |  |
|  | Type - Code |  | 1 phase 2 porcelain |  |
|  | Rated voltage | kV | 15 |  |
|  | Nominal frequency | Hz | 50 |  |
|  | Nominal reactive power output | kVAr | 565 |  |
|  | Rated current | A | 37,67 |  |
|  | Rated Capacitance | µF | 7,99 |  |
|  | Insulation |  | Oil |  |
|  | Dielectric |  | non-PCB |  |
|  | Max. capacitor dielectric losses |  | ≤ 0,1W/kVAr (with test report to prove) This value after calculation has excluded the discharge resistance |  |
|  | Discharge resistor |  | Capacitor has an internal discharge resistor. After disconnecting the capacitor from the grid, the voltage between the two capacitor terminals drops to less than 75V from the initial peak voltage value after 10 minutes (with test report proving it) |  |
|  | Capacitor tank protection |  | there is are fuse in |  |
|  | Maximum allowable working voltage over time at different voltage factors |  | U = 1,1 Un: 12 hours in 24 hours U = 1,15 Un: 30 minutes in 24 hours U = 1,2 Un: 5 minutes U = 1,3 Un: 1 minutes |  |
|  | Permissible Overload Current |  | 1,3xIn |  |
|  | Capacitor unit material |  | stainless steel |  |
|  | Porcelain leakage current minimum | mm/kV | 25 |  |
|  | Dimensions (W x D x H) | mm | offered by Tender |  |
|  | Weight | kg | offered by Tender |  |
| 3 | Complete set of 50 MVAr - 110kV Capacitor bank: |  |  |  |
|  | Installation conditions |  | Outdoor, in substation, altitude up to 1000 m |  |
|  | Environmental conditions |  | Tropicalization, Max. temperature +45oC, Min. temperature 0oC, Max. humidity 100% |  |
|  | Applicable insulation standards |  | IEC 60815 |  |
|  | Manufacturing and testing standards |  | IEC 60871-1 and IEC 60871-2 |  |
|  | Test report |  | Type test issued by independent testing unit |  |
|  | Certificate of quality management system |  | ISO 9001 |  |
|  | Number of capacitors unit/branche | Set | 5 |  |
|  | Number of parallel branches/phase | Branches | 8 |  |
|  | Total capacitors | Set | 120 |  |
|  | Connection scheme |  | Ungrounded-Y-Y |  |
|  | Deviation of capacitance at 20oC with rated capacitance |  | (0 ÷ 10)% |  |
|  | Deviation of capacitance between 2 phase |  | 1,08. |  |
|  | Description of the general principle diagram |  | The application diagram includes a combination of capacitor banks (5 series capacitors /branche and 8 parallel branches/phase), 1 set of 3-phase circuit breakers with 3 separate spring drives, 1 set of 3-phase disconectors, 3 sets of single phase disconectors, 3 set of single phase current transformers, 3 set of single phase voltage transformers, 1 unbalance current transformer, 3 single phase arresters, 3 single phase dry reactor, 1 measurement-control-protection and insulation system, accessories |  |
|  | Capacitor capacity at 110kV |  | 50MVAr |  |
|  | Catalogue of manufactory |  | Yes |  |
|  | Hot dip galvanized steel supporting structure and bolted connection. The brackets are constructed so that any capacitor unit can be removed without disconnecting or removing other capacitors. |  | Yes |  |
|  | Post Insulators must conform to IEC, IEEE standards as well as the EVNNPT's Regulations on Insulator Stands. |  | Yes |  |
|  | Standard-compliant materials are used to connect the capacitors and between the capacitor and the unbalanced current transformer. |  | Yes |  |
|  | Instructions for installation, operation, maintenance, transportation |  | Yes |  |
| 4 | Reactor to limiting discharge current |  |  |  |
|  | Manufacturer/Country of Origin |  | offered by Tender |  |
|  | Year of manufacture |  | offered by Tender |  |
|  | Standard |  | IEC 60076-6 |  |
|  | Type |  | Dry, air core |  |
|  | Design |  | Single phase |  |
|  | Rated voltage |  | 123kV |  |
|  | Frequency |  | 50Hz |  |
|  | Tuning frequency |  | 204Hz |  |
|  | Rated reactance |  | 47.54mH |  |
|  | Power Frequency withstand voltage |  | ≥ 230 kV |  |
|  | Lightning impulse withstand voltage |  | ≥ 550 kVpeak |  |
|  | Rated current (actual rated current) |  | 500A |  |
|  | Breaking capacity to short-circuit current before reactor |  | ≥ 40kA |  |
|  | Breaking capacity to short-circuit current after reactor |  | ≥ 4kA |  |
|  | Hot dip galvanized steel supporting structure and bolted connection |  | Yes |  |
|  | Post Insulators must conform to IEC, IEEE standards as well as the EVNNPT's Regulations on Insulator Stands. |  | Yes |  |
|  | Standard-compliant materials are used to connect the capacitors and between the capacitor and the unbalanced current transformer. |  | Yes |  |
|  | Instructions for installation, operation, maintenance, transportation |  | Yes |  |
| 5 | Unbalance current transformer |  |  |  |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 61869-1, 2 |  |
|  | Type |  | Outdoor, Single phase, oil immersed, Top core, reinforce safety design |  |
|  | Rated voltage | kV | 123 |  |
|  | Frequency | Hz | 50Hz |  |
|  | Impulse Voltage (1.2/50µs) withstand | kV | To be specified |  |
|  | Power Frequency Voltage withstand |  |  |  |
|  | + Primary windings | kV | To be specified |  |
|  | + Secondary windings | kV | To be specified |  |
|  | Housing insulator: |  |  |  |
|  | + Applicable standard |  | To be specified |  |
|  | + Material |  | Brown porcelain |  |
|  | + Minimum nominal creepage distance | mm/kV | 25 |  |
|  | + Minimum nominal specific creepage distance | mm | Comply with IEC 60815 |  |
|  | + Average diameter of insulator |  | To be specified |  |
|  | Rated Primary Current | A | 5 |  |
|  | Phase to Earth Clearance | mm | To be specified |  |
|  | Rated Transformation Ratios | A | 5/1/1A |  |
|  | Core Characteristics: Rated Burden, Accuracy Class |  | 10VA - 5P20 |  |
|  | Hot dip galvanized steel supporting structure and bolted connection |  | yes |  |
| 6 | HV Terminal connectors (Dimensions: Holes - No., size and spacing) |  | yes |  |
|  | Materials |  | offered by Tender |  |
|  | Dimensions |  | offered by Tender |  |
|  | size and No. of holes |  | offered by Tender |  |
|  | Spacing holes |  | offered by Tender |  |
|  | Type test reports |  | To be supplied. |  |
| 7 | Type test reports |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.6 |  |
| 8 | The remaining parameters or different will comply with the provisions of 111/QĐ-HĐTV dated 21/09/2021, 77/QD-HDTV dated 13/03/2025 and 1859/QĐ-EVNNPT dated 28/9/2025 |  | Yes |  |

- POST INSULATOR

  - 220kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Rated voltage | kV | 245 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | To be specified |  |
|  | Dimensions (State Tolerances.): |  |  |  |
| - | Height | mm | To be specified |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | 31 |  |
|  | Minimum nominal specific creepage distance | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 2100 |  |
|  | Minimum insulation breakdown voltage | kV | 1150 |  |
|  | Mechanical |  |  |  |
| - | Minimum Failing Load-bending | kN | 10 |  |
| - | Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | a. Power Frequency Withstand Voltage | kV | 460 |  |
|  | b. Light Impulse Voltage (1.2/50µs) Withstand | kV peak | 1050 |  |
|  | c. 50% Impulse Flashover Voltage |  | To be specified |  |
| - | Positive | kV |  |  |
| - | Negative | kV |  |  |
|  | d. Flashover Voltage |  | To be specified |  |
| - | Dry Flashover Voltage (50 Hz) | kV |  |  |
| - | Wet Flashover Voltage (50 Hz) | kV |  |  |
|  | Fixing Arrangements |  | To be specified |  |
| - | Top Cap PCD | mm |  |  |
| - | Top Cap Fixing Holes - number x size | mm |  |  |
| - | Base PCD |  |  |  |
| - | Base Fixing Holes - number x size |  |  |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |
|  | The remaining parameters or different will comply with the provisions of 0103/QĐ-EVNNPT |  | Yes |  |

  - 110kV Post Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Applicable standard |  | IEC 60273 |  |
|  | Rated voltage | kV | 123 |  |
|  | Insulator material |  | Porcelain |  |
|  | Type |  | To be specified |  |
|  | Dimensions (State Tolerances.): |  |  |  |
| - | Height | mm | To be specified |  |
| - | Average diameter of insulator | mm | To be specified |  |
|  | Minimum nominal creepage distance | mm/kV | 31 |  |
|  | Minimum nominal specific creepage distance | mm | To be specified |  |
|  | Phase to Earth Clearance | mm | ≥ 1100 |  |
|  | Mechanical |  |  |  |
| - | + Minimum Failing Load-bending | kN | 10 |  |
| - | + Minimum Failing Moment-torsion | kNm | 4 |  |
|  | Electrical |  |  |  |
|  | a. Power Frequency Withstand Voltage | kV | 230 |  |
|  | b. Light Impulse Voltage (1.2/50µs) Withstand | kV peak | 550 |  |
|  | c. 50% Impulse Flashover Voltage |  | To be specified |  |
| - | Positive | kV |  |  |
| - | Negative | kV |  |  |
|  | d. Flashover Voltage |  | To be specified |  |
| - | Dry Flashover Voltage (50 Hz) | kV |  |  |
| - | Wet Flashover Voltage (50 Hz) | kV |  |  |
|  | Fixing Arrangements |  | To be specified |  |
| - | Top Cap PCD | mm |  |  |
| - | Top Cap Fixing Holes - number x size | mm |  |  |
| - | Base PCD |  |  |  |
| - | Base Fixing Holes - number x size |  |  |  |
|  | Weight of complete Post Insulator | kg | To be specified |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | To be supplied |  |

  - 22KV POST INSULATOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
| 1 | Manufacture/ Origin of country |  | To be specified |  |
| 2 | Type |  | To be specified |  |
| 3 | IEC destination |  | To be specified |  |
| 4 | Dimensions (State Tolerances.) |  | To be specified |  |
|  | - Height | mm |  |  |
|  | - Diameter | mm |  |  |
|  | - Total Creepage Distance | mm |  |  |
|  | - Protected Creepage Distance | mm |  |  |
|  | - Dry Arcing Distance | mm |  |  |
| 5 | Mechanical |  |  |  |
|  | Minimum Failing Load-bending | kN | 10 |  |
|  | Minimum Failing Moment – torsion | kNm | 1,2 |  |
| 6 | Electrical |  |  |  |
|  | Power Frequency Withstand Voltage |  |  |  |
|  | - Dry Withstand Voltage (1 min. 50Hz) | kV | To be specified |  |
|  | - Wet Withstand Voltage (1 min. 50Hz) | kV | 50 |  |
|  | Light Impulse Withstand Voltage |  |  |  |
|  | - Positive | kV | To be specified |  |
|  | - Negative | kV | 125 |  |
|  | 50% Impulse Flashover Voltage |  |  |  |
|  | - Positive | kV | To be specified |  |
|  | - Negative | kV | To be specified |  |
|  | Flashover Voltage |  |  |  |
|  | - Dry Flashover Voltage (50 Hz) | kV | To be specified |  |
|  | - Wet Flashover Voltage (50 Hz) | kV | To be specified |  |
| 7 | Fixing Arrangements |  |  |  |
|  | Top Cap PCD | mm | To be specified |  |
|  | Top Cap Fixing Holes - number x size | mm | To be specified |  |
|  | Base PCD |  | To be specified |  |
|  | Base Fixing Holes - number x size |  | To be specified |  |
| 8 | Weight |  |  |  |
|  | Complete Post Insulator | kg |  |  |
| 9 | Supporting clamp for : (conductor or Tube, State |  | Yes |  |
| 10 | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 11 | Catalogues |  | To be supplied |  |

- INSULATOR STRINGS

  - 220kV Suspension and Tension Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
| 1 | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
| 2 | Place of factory |  | To be specified |  |
| 3 | Model type: |  |  |  |
| - | Tension insulator |  | U160BSP |  |
| - | Suspension insulator |  | U120BP |  |
| 4 | Insulating material |  | Glass or ceramic |  |
| 5 | Applicable standard |  | IEC 60305 |  |
| 6 | Type of coupling |  | Ball & socket |  |
| 7 | Size of coupling | mm | To be specified |  |
| 8 | Locking device |  | Split pin type |  |
| 9 | Minimum breaking strength: | kN |  |  |
| - | Tension insulator |  | 160 |  |
| - | Suspension insulator |  | 120 |  |
| 10 | Shed diameter (mm) | mm |  |  |
| - | Tension insulator |  | 330 |  |
| - | Suspension insulator |  | 280 |  |
| 11 | Nominal spacing | mm |  |  |
| - | Tension insulator |  | 146 |  |
| - | Suspension insulator |  | 146 |  |
| 12 | Minimum Creepage distance | mm | ≥440 |  |
| 13 | Total creeepage distance | mm | ≥ 7595 |  |
| 14 | Wet power frequency withstand voltage - min | kV |  |  |
| - | Tension insulator |  | 55 |  |
| - | Suspension insulator |  | 50 |  |
| 15 | Dry power frequency withstand voltage-min. | kV |  |  |
| - | Tension insulator |  | 90 |  |
| - | Suspension insulator |  | 85 |  |
| 16 | Dry Lightning impulse withstand: | kV |  |  |
| - | Tension insulator |  | 140 |  |
| - | Suspension insulator |  | 125 |  |
| 17 | Minimum puncture voltage in oil: | kV | 130 |  |
| 18 | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
| 19 | Number of insulator strings in per phase |  | To be specified |  |
| 20 | Min. electro - mechanical failing load complete set: | kN |  |  |
| - | Type single insulator tension string |  | 1 x 160 |  |
| - | Type single insulator suspenion string |  | 1 x 120 |  |
| 21 | Number of insulator disk in each string | disk | 19 |  |
| 22 | Overall length of set including clamp and all fittings |  |  |  |
| - | Max | mm | To be specified |  |
| - | Min | mm | To be specified |  |
| 23 | Weight of complete set with all fittings | kg | To be specified |  |
| 24 | Turnbuckle for 220kV tension insulator |  | Yes |  |
| 25 | Arcing horn for 220kV insulator |  | Yes |  |
| 26 | Fittings type to gantry beam |  | To be specified |  |
|  | Type of fittings |  | U bolt, M18-90 |  |
| 27 | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 28 | Catalogues |  | To be supplied |  |
| (*): The Bidder must calculate the length of insulator string to meet safe clearances showed in Drawings attached to this Bidding Documents. |  |  |  |  |

  - 110kV Suspension and Tension Insulator

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Insulator unit |  |  |  |
| 1 | Manufacturer/Country of Origin of insulator and Fitting of insulator string |  | To be specified |  |
| 2 | Place of factory |  | To be specified |  |
| 3 | Model type |  | U120BP |  |
| 4 | Insulating material |  | Glass or ceramic |  |
| 5 | Applicable standard |  | IEC 60305 |  |
| 6 | Type of coupling |  | Ball & socket |  |
| 7 | Size of coupling | mm | To be specified |  |
| 8 | Locking device |  | Split pin type |  |
| 9 | Minimum breaking strength | kN | ≥ 120 |  |
| 10 | Shed diameter (mm) | mm | To be specified |  |
| 11 | Nominal spacing | mm | 146 |  |
| 12 | Creepage distance - min | mm | ≥440 |  |
| 13 | Total creeepage distance | mm | ≥ 3813 |  |
| 14 | Wet power frequency withstand voltage - min. | kV | 50 |  |
| 15 | Dry power frequency withstand voltage-min. | kV | 85 |  |
| 16 | Dry Lightning impulse withstand | kV | 125 |  |
| 17 | Minimum puncture voltage in oil | kV | 130 |  |
| 18 | Zinc sleeve |  | Yes |  |
|  | Insulator set complete |  |  |  |
| 19 | Number of insulator strings in per phase |  | To be specified |  |
| 20 | Min. electro - mechanical failing load complete set | kN | 1 x 120 |  |
| 21 | Number of insulator disk in each string | disk | 10 |  |
| 22 | Overall length of set including clamp and all fittings |  |  |  |
| - | Max | mm | To be specified |  |
| - | Min | mm | To be specified |  |
| 23 | Weight of complete set with all fittings | kg | To be specified |  |
| 24 | Turnbuckle for 220kV tension insulator |  | Yes |  |
| 25 | Arcing horn for 220kV insulator |  | Yes |  |
| 26 | Fittings type to gantry beam |  | To be specified |  |
|  | Type of fittings |  | U bolt, M18-90 |  |
| 27 | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
| 28 | Catalogues |  | To be supplied |  |
| (*): The Bidder must calculate the length of insulator string to meet safe clearances showed in Drawings attached to this Bidding Documents. |  |  |  |  |

- TUBE AND CONDUCTOR

  - ALUMINUM TUBE Ф160/144

| Item No. | Description | Required | Tendered |
| --- | --- | --- | --- |
| 1 | Manufacture / Country of Origin | To be specified |  |
| 2 | Manufacture's designation and type |  |  |
| 3 | Standards | ASTM-B317, EN 755-2 |  |
| 4 | Material | E-Al Mg Si 0.5 F22 |  |
| 5 | Nominal diameter | Ф160/144 mm |  |
| 6 | Outside diameter | 160mm |  |
| 7 | Inside diameter | 144mm |  |
| 8 | Weight | 10.3kg/m |  |
| 9 | Continuous current-carrying capacity (at ambient temperature 35oC and tube temperature 85oC) | ≥ 4615 A |  |
| 10 | Permissive short circuit current | ≥ 50 kA/1s |  |
| 11 | Tensile strength | ≥ 220 N/mm2 |  |
| 12 | Elongation | 8 % |  |
| 13 | Elasticity modulus | 7.104 N/mm2 |  |
| 14 | Yield strength: |  |  |
| - | Minimum | 160 N/mm2 |  |
| - | Maximum | To be specified |  |
| 15 | Brinell hardness |  |  |
| 16 | Electrical conductivity at 20oC | 30 m/Ωmm2 |  |
| 17 | Type test | To be supplied. The Bidder shall be filled list of test report as shown in item 2.15 |  |
| 18 | Catalogue | Yes |  |

  - ALUMINUM TUBE Ф120/108

| Item No. | Description | Required | Tendered |
| --- | --- | --- | --- |
| 1 | Manufacture / Country of Origin | To be specified |  |
| 2 | Manufacture's designation and type |  |  |
| 3 | Standards | ASTM-B317, EN 755-2 |  |
| 4 | Material | E-Al Mg Si 0.5 F22 |  |
| 5 | Nominal diameter | Ф120/108 mm |  |
| 6 | Outside diameter | 120 mm |  |
| 7 | Inside diameter | 108 mm |  |
| 8 | Weight | 5.8 kg/m |  |
| 9 | Continuous current-carrying capacity (at ambient temperature 35oC and tube temperature 85oC) | ≥ 3115A |  |
| 10 | Permissive short circuit current | ≥ 31.5 kA/1s |  |
| 11 | Tensile strength | ≥ 220 N/mm2 |  |
| 12 | Elongation | 8 % |  |
| 13 | Elasticity modulus | 7.104 N/mm2 |  |
| 14 | Yield strength: |  |  |
| - | Minimum | 160 N/mm2 |  |
| - | Maximum | To be specified |  |
| 15 | Brinell hardness |  |  |
| 16 | Electrical conductivity at 20oC | 30 m/Ωmm2 |  |
| 17 | Type test | To be supplied. The Bidder shall be filled list of test report as shown in item 2.15 |  |
| 18 | Catalogue | Yes |  |

  - AAC-630

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | IEC 61089 |  |
|  | Type |  | AAC-630 |  |
|  | Nominal cross section area: | mm2 | 630 |  |
|  | Stranded number and diameter of strands | mm | To be specified |  |
|  | Stranding direction of outer most layer |  | To be specified |  |
|  | Minimum strength load | N | ≥ 100800 |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor | kg/km | To be specified |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C | A | To be specified |  |
|  | Overall diameter of stranded conductor | mm | To be specified |  |
|  | DC resistance at 200C | Ω/km | ≤ 0,0515 |  |
|  | Type test and routine test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogues |  | Yes |  |

  - ACSR-185/29-XLPE/HDPE

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacturer/ Country of Origin |  | To be specified |  |
|  | Designation |  | To be specified |  |
|  | Standard |  | TCVN 5064-94 |  |
|  | Type |  | ACSR-185/29-XLPE/HDPE |  |
|  | Nominal cross section area: |  |  |  |
|  | - Aluminum | mm2 | 185 |  |
|  | - Steel | mm2 | 29 |  |
|  | Stranded number and diameter of strands |  |  |  |
|  | - Aluminum | mm | 26/2.98 |  |
|  | - Steel | mm | 7/2.3 |  |
|  | Thickness of insulation XLPE (Approx.) | mm | 5.5 |  |
|  | Thickness of outer sheat HDPE (Approx.) | mm | 1.2 |  |
|  | Overall diameter (Approx.) | mm | 32.9 |  |
|  | Minimum strength load | kN | ≥ 62.06 |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |
|  | Maximum mass of conductor | kg/km | To be specified |  |
|  | Type test |  | To be supplied |  |
|  | Continuous current capacity at max. operating temperature of 900C and in air of 250C | A | To be specified |  |
|  | Overall diameter of stranded conductor | mm | To be specified |  |
|  | Resistance DC calculated at 200C | Ω/km | ≤ 0.1591 |  |
|  | Modulus of elasticity of conductor | daN/mm2 | To be specified |  |

- HV CONNECTOR

| Item No. | Description | Unit | Required | Offered |
| --- | --- | --- | --- | --- |
|  | Manufacture/ Country of Origin |  | To be specified |  |
|  | Place of factory |  | To be specified |  |
|  | Ordering number |  | To be specified |  |
|  | Applicable standard |  | IEC 694, NEMA CC1 or equivalent |  |
|  | Type |  | Aluminium alloy |  |
|  | Slip strength of bolted connnector |  | To be specified |  |
|  | Bolt and screw of connector |  | Galvanized steel |  |
|  | Short-time withstand current |  |  |  |
|  | + 220kV side | kA/1s | 50 |  |
|  | + 110kV side | kA/1s | 40 |  |
|  | + 22kV side | kA/1s | 25 |  |
|  | Number holes (Min 06 holes) |  | Comply |  |
|  | Tightening force for bolt |  |  |  |
|  | - M10 bolt |  | To be specified |  |
|  | - M12 bolt |  | To be specified |  |
|  | - M14 bolt |  | To be specified |  |
|  | - M16 bolt |  | To be specified |  |
|  | Contact grease: |  | Yes |  |
|  | - Manufacture/ Country of Origin |  | To be specified |  |
|  | - Quantity |  | Conformity with connector |  |
|  | Type test |  | To be supplied. The Bidder shall be filled list of test report as shown in item 2.14 |  |
|  | Catalogue |  | Yes |  |