Attachment No.1 – Scope of Work/Services

to ITB No. PVEPNCS-26-10239

Provision of Rental Services for the Ruston Gas Turbine TB5000 Gas Generator Section for RGT-B at FPU ĐH-01, Block 05-1(a), Offshore Vietnam

- Introduction:

On the PVEP-NCS DH-01 Floating Platform Unit (FPU) there are two Ruston Gas Turbines:

      - Ruston Gas Turbine TB 5000 – A

      - Ruston Gas Turbine TB 5000 – B

Manufacturer is Ruston Turbine Lincoln, England. Both Gas turbines have the same technical characters as below:

Drive:

Turbine Type: TB5000

S/N: TB5000/500

Engine No: 9052/1284-2, two shaft

Turbine shaft speed: 7950 rpm/min and 8750 Rpm/max

Load Gearbox: Allen Gear.

Alternator:

GEC three phase generator,

Type: Unipak BJSH 11/4

S/N: 44106002

Number of Pole: 4 poles

RPM: 1800

6.6KV / 3 phase / 60Hz

Rated Electrical Power:  3.355MW – 4.194MW

- Background and objective

The engine is a two-shaft unit and consists of two main sections: the gas generator and the power turbine.

The gas generator section is made up of air inlet casing, compressor stator casing, compressor turbine stator casing, center casing, combustion chambers and rotor assembly.

The power turbine comprises the power turbine stator assembly, exhaust collector assembly and power turbine rotor assembly from which the drive is transmitted to the gearbox and driven machinery via a gear type sleeve coupling.

During the execution of repair works on the exhaust outlet duct diffuser for the RGT-B, significant metal debris was discovered at the second-stage turbine compressor blades. Following the complete disassembly, inspection, and damage assessment of the gas generator assembly, an abnormal rotor assembly axial displacement exceeding 2.18 mm was identified. This critical displacement caused severe damage to the associated components due to excessive friction between the rotating and stationary parts.

The damaged gas generator assembly must undergo a comprehensive repair and overhaul. To guarantee uninterrupted operations of the power generation system on the FPU-DH01 during this overhaul period, the PVEPNCS is seeking to rent a replacement gas generator unit for the Ruston Gas Turbine TB5000 with equivalent technical specifications.

- TECHNICAL & OPERATIONAL REQUIREMENTS

Equipment Condition: The rented gas generator assembly must be supplied in pristine, flawless condition and be fully ready for immediate operation. All operational parameters and physical installation dimensions must be 100% compatible with the existing damaged unit.

Quality Assurance & Documentation: The Contractor must submit an inspection report on the equipment's condition prior to handover for installation at FPU ĐH-01, confirming that the rented gas generator assembly is in pristine, flawless condition and fully ready for immediate operation.

Logistics & Field Execution: The Contractor is solely responsible for providing all necessary personnel, specialized tooling, and equipment to execute the transportation of the gas generator to the offshore FPU-DH01, seamless integration into the system, commissioning, and final inspection/acceptance testing.

- TEAM LEADER COMPETENCY REQUIREMENTS

The Contractor must submit a comprehensive Curriculum Vitae (CV) for the assigned Team Leader. The candidate must demonstrate a minimum of five (5) years of direct hands-on experience in the maintenance, troubleshooting, and overhaul of the Ruston Gas Turbine TB5000 series.

- COMMERCIAL, RENTAL BASIS & MAINTENANCE CONDITIONS

Rate Calculation: The rental fee for the equipment shall be calculated based on the actual number of operational days or running hours clocked by the unit.

Unscheduled Shutdowns (Downtime): In the event of a machine shutdown where the root cause is determined to be a fault within the Contractor’s rented equipment, the rental fee for that specific downtime period will be strictly non-payable.

Contract Duration & Invoicing: The total validity of this rental contract is six (6) months, with payments processed and settled on a operational days/running hours/ monthly basis.

Delivery time: Upon contract signing, the Contractor must deliver the goods within a maximum of 3 working days after receiving a delivery request via mail or email.

- HEALTH, SAFETY, AND ENVIRONMENT (HSE) REQUIREMENTS

All potential risks to personnel posed by the Vendor's activities must be thoroughly assessed and minimized in strict compliance with PVEPNCS HSE regulations.

All personnel deployed by the Vendor to work on the DH-01 platform must strictly adhere to the designated DH-01 HSE regulations.

All onsite personnel are required to actively participate in all daily Toolbox Meetings and Safety Briefings.

Work Location: FPU ĐH-01, Dai Hung Field.